## Frontpage
Modbus/BACnet Protocol
67500A 03/19 (OSH)
c 2019 OJ Electronics A/S

## Info
© 2018 OJ Electronics A/S · ® The OJ trademark is a registered trademark belonging to OJ Electronics A/S
OJ Green Zone Master
Modbus and BACnet protocol
Software version 3.40
BTL certificate
BACnet conformance certificate
Connections
Connecting the OJ-Green Zone to BMS
Modbus Info
General information about modbus RTU/TCP-IP
BACnet Info
General information about BACnet TCP-IP
Parameters
Complete list of all modbus and BACnet parameters.
BitMap
Alarm overview

## Connections
© 2019 OJ Electronics A/S · ® The Trade Mark OJ is an registered Trade Mark belonging to OJ Electronics A/S
OJ Green Zone Master Controller
1 x RJ45 TCP/IP connection to BMS system
Fig. 1 OJ Green Zone Master, RJ45 for TCP/IP BMS
Fig. 2 Multiple OJ Green Zone Master in a BMS system

## Modbus info
Modbus TCP-IP
OJ GreenZone™ Master, Program Version 1.00 and subsequent versions.
Introduction
With the built-in Modbus TCP/IP protocol, it is possible to monitor, manage and control an OJ GreenZone™ system from a BMS system.
Communication
TCP/IP: 1 x 10/100 Mbit Ethernet, RJ45 connector
Port: 502
IP address: The same as the OJ GreenZone™ Master's Web server.
Modbus data format
Modbus data types are 1-bit values and 16-bit values.
ModBus Type |  | Description | Reference
Coli Status (R/W) |  | Discrete Output | 0x
Input Status (R) |  | Discrete Input | 1x
Holding Register (R/W) |  | 16-bit Output Register | 4x
Input register (R) |  | 16-bit Input Register | 3x
R = Read Only
R/W = Read/Write
Supported Modbus commands
OJ GreenZone™ Master supports the following Modbus commands.
Function code | Description
01 | Read Coil Status
02 | Read Input Status
03 | Read Holding Registers
04 | Read Input Registers
05 | Force Single Coil
06 | Present Single Registers
08 | Diagnostics.Sub-funktion 00 Only - Return Query Data (loop back).
15 | Force Multiple Coils
16 | Preset Multiple Registers
6 | Preset Single Registers
8 | Diagnostics. Sub-function 00 Only - Return Query Data (loop back)
15 | Force Multiple Coils
16 | Preset Multiple Registers
© 2019 OJ Electronics A/S · ® The OJ trademark is a registered trademark belonging to OJ Electronics A/S

## Modbus Overview parameters (hidden)
Actual extract flow [l/s] |  |  | 3x0009
Extract motor output percentage [1/100%] |  |  | 3x0083 |  |  |  | Actual operating mode | 3x0001
Setpoint for extract flow, low speed [l/s] |  |  | 4x0014 |  |  |  | Operation ON/OFF | 1x0001
Setpoint for extract flow, high speed [l/s] |  |  | 4x0015 |  |  |  | Extended low speed –> Active | 1x0004
[7 empty] | Extended high speed –> Active | 1x0005
|  | Actual extract duct pressure [Pa] |  | 3x0005 |  |  | Alarm relay 1 (A-alarm) | 1x0035
|  | Setpoint for duct pressure, extract, low speed [Pa] |  | 4x0007 |  |  | Alarm relay 2 (B-alarm) | 1x0036
|  | Setpoint for duct pressure, extract, high speed [Pa] |  | 4x0008 |  |  | Alarm reset signal (AutoReturn to zero) | 0x0001
|  | Inlet filter pressure [Pa] |  | 3x0031
|  | Inlet filter monitor max. alarm limit [Pa] |  | 3x0039
[7 empty] | Actual inlet temperature [1/100°C] | 3x0020
[7 empty] | Control type setting | 4x0148
[7 empty] | Temperature setpoint for actual control type | 4x0149
[7 empty] | Extract filter pressure [Pa] | 3x0032
[7 empty] | Max. alarm limit, extract filter pressure drop [Pa] | 3x0040
[7 empty] | Actual room temperature [1/100 °C] | 3x0025
[7 empty] | Actual exhaust temp. [1/100°C] | 3x0026
[7 empty] | Min. limit, inlet temp. [1/100°C] | 4x0150
[7 empty] | Max. limit, inlet temp. [1/100°C] | 4x0151
[7 empty] | Actual inlet duct pressure [Pa] | 3x0003
[7 empty] | Setpoint for duct pressure, inlet, low speed [Pa] | 4x0003
[7 empty] | Setpoint for duct pressure, inlet, high speed [Pa] | 4x0004
[7 empty] | Actual inlet flow [l/s] | 3x0007
[7 empty] | Inlet motor output percentage [1/100%] | 3x0073
[7 empty] | Setpoint for inlet flow, low speed [l/s] | 4x0011
[7 empty] | Setpoint for inlet flow, high speed [l/s] | 4x0012
Actual outdoor temp. [1/100°C] 3x0024 |  |  |  |  | Actual heating power [1/100%] | 3x0054
[5 empty] | Heating relay 1 | 1x0031
| Rot. heat exchanger – output percent. [%] |  | 3x0092 |  | Act. heating bat. temp.[1/100°C] | 3x0030
|  |  | Actual cooling power [1/100%] |  | 3x0056
© 2016 OJ Electronics A/S · ® The Trade Mark OJ is an registered Trade Mark belonging to OJ Electronics A/S
06-07-16

## BacNet info
BACnet
OJ Green Zone Master, Program version 1.00 and future versions
Overview
With the integrated BACnet TCP / IP protocol, it is possible to control, manage
and monitor an OJ Green Zone system from a BMS system.
BACnet functionality is implemented in OJ Green Zone Master with software
version 1.00 or higher
OJ Green Zone Master is a BACnet Application Specific Controller (B-ASC)
Supportered Data Link Layer Options: BACnet IP
Further information regarding BACnet as eg OJ Green Zone Master PICS and EDE
data may be obtained and downloaded at www.ojelectronics.com
Communikation
TCP/IP: 1 piece 10/100Mbit Ethernet, RJ45 plug
Object Indentifier:
Object_Identifier is automatically set to the last 5 digits of OJ Green Zone Master's IP address
Example: IP-address = 172.21.0.95 ………………..…….. Object Identifier = 95
IP-address = 155.37.0.216 ………………....... Object Identifier = 216
IP-adress = 155.37.35.123 ………………..... Object Identifier = 35123
IP-adress = 132.65.124.103 ……………….. Object Identifier = 24103
IP-adress = 172.20.211.47 ………………..... Object Identifier = 11047
IP-adress = 155.37.111.123 ………………... Object Identifier = 11123
IP-adress = 168.25.111.1 ………………..….. Object Identifier = 11001
Max. 300 values ​​can be entered to COV (Change Of Value)
BACnet Interoperability Building Blocks Supported
Data Sharing |  |  | DS-RP-B | Data Sharing-Read Property-B
Data sharing |  |  | DS-WP-B | Data Sharing-Write Property-B
Device Management |  |  | DM-DDB-B | Device Management-Dynamic Device Binding-B
Device Management |  |  | DM-DOB-B | Device Management-Dynamic Object Binding-B
Device Management |  |  | DM-DCC-B | Device Management-Dynamic Communication Control-B
Standard Object Types Supported
Object type |  | Properties
Analog Input |  | Object_Identifier, Object_Name, Object_Type, Present_Value, Status_Flags, Event_State, Out_Of_Service, Units, Min_Pres_Value, Max_Pres_Value, Resolution, Reliability, COV_Increment
Analog Value |  | Object_Identifier, Object_Name, Object_Type, Present_Value, Status_Flags, Event_State, Out_Of_Service, Units, Priority_Array, Relinquish_Default, COV_Increment.
Binary Input |  | Object_Identifier, Object_Name, Object_Type, Present_Value, Status_Flags, Event_State, Out_Of_Service, Polarity.
Binary Value |  | Object_Identifier, Object_Name, Object_Type, Present_Value, Status_Flags, Event_State, Out_Of_Service, Priority_Array, Relinquish_Default.
Device |  | Object_Identifier, Object_Name, Object_Type, System_Status, Vendor_Name, Vendor_Identifier, Model_Name, Firmware_Revision, Aplication_Software_Version, Location, Description, Protocol_Version, Protocol_Revision, Protocol_Services_Supported, Protocol_Object_Types_Supported, Object_list, Max_APDU_Length_Accepted, Segmentation_Supported, APDU_Timeout, Number_Of_APDU_Retries, Device_Address_Binding, Database_Revision.

## Parameters
Intern ID | Name | SI Unit | Modbus register | SW vers. | BacNet parameter | SW vers. | Min | Max | Description | Dansk | English
| 1. Info |  | Coil status (R/W) |  | Binary value (R/W) | 1. Info | 1. Info | 1. Info
0x0E00 | Automatic Daylight Saving Time | n/a | 0x0001 |  | BV0 |  | 0 | 1 |  |  | Automatic summer/winter time [1=Yes/0=No]
0x0002 | Summer/Winter Compensation Enable | n/a | 0x0101 |  | BV100 |  | 0 | 1 |  |  | Summer/winter compensation [1=Yes/0=No]
0x0370 | DIN Start (BMS) | n/a | 0x0104 | 3.30 | BV103 | 3.30 | 0 | 1 |  |  | Start via BMS - only active if Coil Status 0x0111 is = "1" (active)
0x0380 | DIN Fire (BMS) | n/a | 0x0105 | 3.30 | BV104 | 3.30 | 0 | 1 |  |  | Fire alarm from BMS - only active if Coil Status 0x0111 is = "1" (active)
0x03C0 | DIN Max Air (BMS) | n/a | 0x0106 | 3.30 | BV105 | 3.30 | 0 | 1 |  |  | Override to max air volume via BMS - only active if Coil Status 0x0111 is = "1" (active)
0x03E0 | DIN Min Air (BMS) | n/a | 0x0107 | 3.30 | BV106 | 3.30 | 0 | 1 |  |  | Override to min air volume via BMS - only active if Coil Status 0x0111 is = "1" (active)
0x0420 | DIN Combi-Heat Available (BMS) | n/a | 0x0108 | 3.30 | BV107 | 3.30 | 0 | 1 |  |  | Hot water available for Combi coil - only active if Coil Status 0x0111 is = "1" (active)
0x0800 | DIN Combi-Cool Available (BMS) | n/a | 0x0109 | 3.30 | BV108 | 3.30 | 0 | 1 |  |  | Cold water available for Combi coil - only active if Coil Status 0x0111 is = "1" (active)
0x0810 | DIN Summer Night Cooling (BMS) | n/a | 0x0110 | 3.30 | BV109 | 3.30 | 0 | 1 |  |  | Summer night cooling start via BMS - only active if Coil Status 0x0111 is = "1" (active)
0x0811 | Enable Digital Input Values from BMS | n/a | 0x0111 | 3.30 | BV110 | 3.30 | 0 | 1 |  |  | Enable Coil Status 0x0104….0x0110; * If this register 0x0111 is "0", the status on register 0x0104….0x0110 are ignored
0x0008 | Week Schedule Enabled in Zones | n/a | 0x0112 | 3.30 | BV111 | 3.30 | 0 | 1 |  |  | Enable week schedule in the zones
0x0812 | Clear All Alarms (BMS) | n/a | 0x0113 | 3.30 | BV112 | 3.30 | 0 | 1 |  |  | Clear all alarms from BMS
| 1. Info |  | Input status (R) |  | Binary input (R) | 1. Info | 1. Info | 1. Info
0x1000 | AHU Heating Pump State | n/a | 1x0101 |  | BI100 |  | 0 | 1 |  |  | Circulationpump, heatsupply
0x1001 | Section PIR Status | n/a | 1x0301 |  | BI300 |  | 0 | 1 |  |  | PIR state; Min. 1 OJ Green Zone is activated through the PIR sensor
0x1002 | Section Frost Protection Status | n/a | 1x0302 |  | BI301 |  | 0 | 1 |  |  | Frost state; Min. 1 frost thermostat in OJ Green Zone is activated [Frostalarm]
0x1810 | ZoneModule 1 - Window/Frost Value | n/a | 1x1001 |  | BI1000 |  | 0 | 1 |  |  | State on input "Window/Frost" - Zone 1 * Is the input configured as window contact, the window is closed when state is "1" * Is the input configured as frost thermostat, then frostalarm is activ when state is "0"
0x1811 | ZoneModule 1 - PIR Active Flag | n/a | 1x1002 |  | BI1001 |  | 0 | 1 |  |  | PIR movement sensor activated - Zone 1
0x1013 | ZoneModule 1 - Room Temp Sensor Short Circuit Flag | n/a | 1x1003 |  | BI1002 |  | 0 | 1 |  |  | Roomtemperatur sensor short circuit - Zone 1
0x1812 | ZoneModule 1 - Supply Temp Sensor Short Circuit Flag | n/a | 1x1004 |  | BI1003 |  | 0 | 1 |  |  | Supply temperature sensor short circuit - Zone 1
0x1341 | ZoneModule 2 - Window/Frost Value | n/a | 1x1101 |  | BI1100 |  | 0 | 1 |  |  | State on input "Window/Frost" - Zone 2 * Is the input configured as window contact, the window is closed when state is "1" * Is the input configured as frost thermostat, then frostalarm is activ when state is "0"
0x1370 | ZoneModule 2 - PIR Active Flag | n/a | 1x1102 |  | BI1101 |  | 0 | 1 |  |  | PIR movement sensor activated - Zone 2
0x1371 | ZoneModule 2 - Room Temp Sensor Short Circuit Flag | n/a | 1x1103 |  | BI1102 |  | 0 | 1 |  |  | Roomtemperatur sensor short circuit - Zone 2
0x1380 | ZoneModule 2 - Supply Temp Sensor Short Circuit Flag | n/a | 1x1104 |  | BI1103 |  | 0 | 1 |  |  | Supply temperature sensor short circuit - Zone 2
0x1381 | ZoneModule 3 - Window/Frost Value | n/a | 1x1201 |  | BI1200 |  | 0 | 1 |  |  | State on input "Window/Frost" - Zone 3 * Is the input configured as window contact, the window is closed when state is "1" * Is the input configured as frost thermostat, then frostalarm is activ when state is "0"
0x13D0 | ZoneModule 3 - PIR Active Flag | n/a | 1x1202 |  | BI1201 |  | 0 | 1 |  |  | PIR movement sensor activated - Zone 3
0x13E1 | ZoneModule 3 - Room Temp Sensor Short Circuit Flag | n/a | 1x1203 |  | BI1202 |  | 0 | 1 |  |  | Roomtemperatur sensor short circuit - Zone 3
0x100D | ZoneModule 3 - Supply Temp Sensor Short Circuit Flag | n/a | 1x1204 |  | BI1203 |  | 0 | 1 |  |  | Supply temperature sensor short circuit - Zone 3
0x1321 | ZoneModule 4 - Window/Frost Value | n/a | 1x1301 |  | BI1300 |  | 0 | 1 |  |  | State on input "Window/Frost" - Zone 4 * Is the input configured as window contact, the window is closed when state is "1" * Is the input configured as frost thermostat, then frostalarm is activ when state is "0"
0x1103 | ZoneModule 4 - PIR Active Flag | n/a | 1x1302 |  | BI1301 |  | 0 | 1 |  |  | PIR movement sensor activated - Zone 4
0x1104 | ZoneModule 4 - Room Temp Sensor Short Circuit Flag | n/a | 1x1303 |  | BI1302 |  | 0 | 1 |  |  | Roomtemperatur sensor short circuit - Zone 4
0x1203 | ZoneModule 4 - Supply Temp Sensor Short Circuit Flag | n/a | 1x1304 |  | BI1303 |  | 0 | 1 |  |  | Supply temperature sensor short circuit - Zone 4
0x1204 | ZoneModule 5 - Window/Frost Value | n/a | 1x1401 |  | BI1400 |  | 0 | 1 |  |  | State on input "Window/Frost" - Zone 5 * Is the input configured as window contact, the window is closed when state is "1" * Is the input configured as frost thermostat, then frostalarm is activ when state is "0"
0x1003 | ZoneModule 5 - PIR Active Flag | n/a | 1x1402 |  | BI1401 |  | 0 | 1 |  |  | PIR movement sensor activated - Zone 5
0x1332 | ZoneModule 5 - Room Temp Sensor Short Circuit Flag | n/a | 1x1403 |  | BI1402 |  | 0 | 1 |  |  | Roomtemperatur sensor short circuit - Zone 5
0x1333 | ZoneModule 5 - Supply Temp Sensor Short Circuit Flag | n/a | 1x1404 |  | BI1403 |  | 0 | 1 |  |  | Supply temperature sensor short circuit - Zone 5
0x1350 | ZoneModule 6 - Window/Frost Value | n/a | 1x1501 |  | BI1500 |  | 0 | 1 |  |  | State on input "Window/Frost" - Zone 6 * Is the input configured as window contact, the window is closed when state is "1" * Is the input configured as frost thermostat, then frostalarm is activ when state is "0"
0x1402 | ZoneModule 6 - PIR Active Flag | n/a | 1x1502 |  | BI1501 |  | 0 | 1 |  |  | PIR movement sensor activated - Zone 6
0x1460 | ZoneModule 6 - Room Temp Sensor Short Circuit Flag | n/a | 1x1503 |  | BI1502 |  | 0 | 1 |  |  | Roomtemperatur sensor short circuit - Zone 6
0x1461 | ZoneModule 6 - Supply Temp Sensor Short Circuit Flag | n/a | 1x1504 |  | BI1503 |  | 0 | 1 |  |  | Supply temperature sensor short circuit - Zone 6
0x1922 | ZoneModule 7 - Window/Frost Value | n/a | 1x1601 |  | BI1600 |  | 0 | 1 |  |  | State on input "Window/Frost" - Zone 7 * Is the input configured as window contact, the window is closed when state is "1" * Is the input configured as frost thermostat, then frostalarm is activ when state is "0"
0x1400 | ZoneModule 7 - PIR Active Flag | n/a | 1x1602 |  | BI1601 |  | 0 | 1 |  |  | PIR movement sensor activated - Zone 7
0x1420 | ZoneModule 7 - Room Temp Sensor Short Circuit Flag | n/a | 1x1603 |  | BI1602 |  | 0 | 1 |  |  | Roomtemperatur sensor short circuit - Zone 7
0x1921 | ZoneModule 7 - Supply Temp Sensor Short Circuit Flag | n/a | 1x1604 |  | BI1603 |  | 0 | 1 |  |  | Supply temperature sensor short circuit - Zone 7
0x1480 | ZoneModule 8 - Window/Frost Value | n/a | 1x1701 |  | BI1700 |  | 0 | 1 |  |  | State on input "Window/Frost" - Zone 8 * Is the input configured as window contact, the window is closed when state is "1" * Is the input configured as frost thermostat, then frostalarm is activ when state is "0"
0x1481 | ZoneModule 8 - PIR Active Flag | n/a | 1x1702 |  | BI1701 |  | 0 | 1 |  |  | PIR movement sensor activated - Zone 8
0x1488 | ZoneModule 8 - Room Temp Sensor Short Circuit Flag | n/a | 1x1703 |  | BI1702 |  | 0 | 1 |  |  | Roomtemperatur sensor short circuit - Zone 8
0x1489 | ZoneModule 8 - Supply Temp Sensor Short Circuit Flag | n/a | 1x1704 |  | BI1703 |  | 0 | 1 |  |  | Supply temperature sensor short circuit - Zone 8
0x1485 | ZoneModule 9 - Window/Frost Value | n/a | 1x1801 |  | BI1800 |  | 0 | 1 |  |  | State on input "Window/Frost" - Zone 9 * Is the input configured as window contact, the window is closed when state is "1" * Is the input configured as frost thermostat, then frostalarm is activ when state is "0"
0x1E3D | ZoneModule 9 - PIR Active Flag | n/a | 1x1802 |  | BI1801 |  | 0 | 1 |  |  | PIR movement sensor activated - Zone 9
0x1390 | ZoneModule 9 - Room Temp Sensor Short Circuit Flag | n/a | 1x1803 |  | BI1802 |  | 0 | 1 |  |  | Roomtemperatur sensor short circuit - Zone 9
0x1391 | ZoneModule 9 - Supply Temp Sensor Short Circuit Flag | n/a | 1x1804 |  | BI1803 |  | 0 | 1 |  |  | Supply temperature sensor short circuit - Zone 9
0x1322 | ZoneModule 10 - Window/Frost Value | n/a | 1x1901 |  | BI1900 |  | 0 | 1 |  |  | State on input "Window/Frost" - Zone 10 * Is the input configured as window contact, the window is closed when state is "1" * Is the input configured as frost thermostat, then frostalarm is activ when state is "0"
0x13B1 | ZoneModule 10 - PIR Active Flag | n/a | 1x1902 |  | BI1901 |  | 0 | 1 |  |  | PIR movement sensor activated - Zone 10
0x1394 | ZoneModule 10 - Room Temp Sensor Short Circuit Flag | n/a | 1x1903 |  | BI1902 |  | 0 | 1 |  |  | Roomtemperatur sensor short circuit - Zone 10
0x1395 | ZoneModule 10 - Supply Temp Sensor Short Circuit Flag | n/a | 1x1904 |  | BI1903 |  | 0 | 1 |  |  | Supply temperature sensor short circuit - Zone 10
0x1100 | ZoneModule 11 - Window/Frost Value | n/a | 1x2001 |  | BI2000 |  | 0 | 1 |  |  | State on input "Window/Frost" - Zone 11 * Is the input configured as window contact, the window is closed when state is "1" * Is the input configured as frost thermostat, then frostalarm is activ when state is "0"
0x1200 | ZoneModule 11 - PIR Active Flag | n/a | 1x2002 |  | BI2001 |  | 0 | 1 |  |  | PIR movement sensor activated - Zone 11
0x1300 | ZoneModule 11 - Room Temp Sensor Short Circuit Flag | n/a | 1x2003 |  | BI2002 |  | 0 | 1 |  |  | Roomtemperatur sensor short circuit - Zone 11
0x1310 | ZoneModule 11 - Supply Temp Sensor Short Circuit Flag | n/a | 1x2004 |  | BI2003 |  | 0 | 1 |  |  | Supply temperature sensor short circuit - Zone 11
0x1320 | ZoneModule 12 - Window/Frost Value | n/a | 1x2101 |  | BI2100 |  | 0 | 1 |  |  | State on input "Window/Frost" - Zone 12 * Is the input configured as window contact, the window is closed when state is "1" * Is the input configured as frost thermostat, then frostalarm is activ when state is "0"
0x1330 | ZoneModule 12 - PIR Active Flag | n/a | 1x2102 |  | BI2101 |  | 0 | 1 |  |  | PIR movement sensor activated - Zone 12
0x1920 | ZoneModule 12 - Room Temp Sensor Short Circuit Flag | n/a | 1x2103 |  | BI2102 |  | 0 | 1 |  |  | Roomtemperatur sensor short circuit - Zone 12
0x1331 | ZoneModule 12 - Supply Temp Sensor Short Circuit Flag | n/a | 1x2104 |  | BI2103 |  | 0 | 1 |  |  | Supply temperature sensor short circuit - Zone 12
0x1428 | ZoneModule 13 - Window/Frost Value | n/a | 1x2201 |  | BI2200 |  | 0 | 1 |  |  | State on input "Window/Frost" - Zone 13 * Is the input configured as window contact, the window is closed when state is "1" * Is the input configured as frost thermostat, then frostalarm is activ when state is "0"
0x1429 | ZoneModule 13 - PIR Active Flag | n/a | 1x2202 |  | BI2201 |  | 0 | 1 |  |  | PIR movement sensor activated - Zone 13
0x142A | ZoneModule 13 - Room Temp Sensor Short Circuit Flag | n/a | 1x2203 |  | BI2202 |  | 0 | 1 |  |  | Roomtemperatur sensor short circuit - Zone 13
0x142B | ZoneModule 13 - Supply Temp Sensor Short Circuit Flag | n/a | 1x2204 |  | BI2203 |  | 0 | 1 |  |  | Supply temperature sensor short circuit - Zone 13
0x142C | ZoneModule 14 - Window/Frost Value | n/a | 1x2301 |  | BI2300 |  | 0 | 1 |  |  | State on input "Window/Frost" - Zone 14 * Is the input configured as window contact, the window is closed when state is "1" * Is the input configured as frost thermostat, then frostalarm is activ when state is "0"
0x1101 | ZoneModule 14 - PIR Active Flag | n/a | 1x2302 |  | BI2301 |  | 0 | 1 |  |  | PIR movement sensor activated - Zone 14
0x1102 | ZoneModule 14 - Room Temp Sensor Short Circuit Flag | n/a | 1x2303 |  | BI2302 |  | 0 | 1 |  |  | Roomtemperatur sensor short circuit - Zone 14
0x1A40 | ZoneModule 14 - Supply Temp Sensor Short Circuit Flag | n/a | 1x2304 |  | BI2303 |  | 0 | 1 |  |  | Supply temperature sensor short circuit - Zone 14
0x1A41 | ZoneModule 15 - Window/Frost Value | n/a | 1x2401 |  | BI2400 |  | 0 | 1 |  |  | State on input "Window/Frost" - Zone 15 * Is the input configured as window contact, the window is closed when state is "1" * Is the input configured as frost thermostat, then frostalarm is activ when state is "0"
0x1A42 | ZoneModule 15 - PIR Active Flag | n/a | 1x2402 |  | BI2401 |  | 0 | 1 |  |  | PIR movement sensor activated - Zone 15
0x1A43 | ZoneModule 15 - Room Temp Sensor Short Circuit Flag | n/a | 1x2403 |  | BI2402 |  | 0 | 1 |  |  | Roomtemperatur sensor short circuit - Zone 15
0x1A44 | ZoneModule 15 - Supply Temp Sensor Short Circuit Flag | n/a | 1x2404 |  | BI2403 |  | 0 | 1 |  |  | Supply temperature sensor short circuit - Zone 15
0x1EB8 | ZoneModule 16 - Window/Frost Value | n/a | 1x2501 |  | BI2500 |  | 0 | 1 |  |  | State on input "Window/Frost" - Zone 16 * Is the input configured as window contact, the window is closed when state is "1" * Is the input configured as frost thermostat, then frostalarm is activ when state is "0"
0x1A46 | ZoneModule 16 - PIR Active Flag | n/a | 1x2502 |  | BI2501 |  | 0 | 1 |  |  | PIR movement sensor activated - Zone 16
0x1A45 | ZoneModule 16 - Room Temp Sensor Short Circuit Flag | n/a | 1x2503 |  | BI2502 |  | 0 | 1 |  |  | Roomtemperatur sensor short circuit - Zone 16
0x1201 | ZoneModule 16 - Supply Temp Sensor Short Circuit Flag | n/a | 1x2504 |  | BI2503 |  | 0 | 1 |  |  | Supply temperature sensor short circuit - Zone 16
0x1A61 | ZoneModule 17 - Window/Frost Value | n/a | 1x2601 |  | BI2600 |  | 0 | 1 |  |  | State on input "Window/Frost" - Zone 17 * Is the input configured as window contact, the window is closed when state is "1" * Is the input configured as frost thermostat, then frostalarm is activ when state is "0"
0x1A62 | ZoneModule 17 - PIR Active Flag | n/a | 1x2602 |  | BI2601 |  | 0 | 1 |  |  | PIR movement sensor activated - Zone 17
0x1A63 | ZoneModule 17 - Room Temp Sensor Short Circuit Flag | n/a | 1x2603 |  | BI2602 |  | 0 | 1 |  |  | Roomtemperatur sensor short circuit - Zone 17
0x1A64 | ZoneModule 17 - Supply Temp Sensor Short Circuit Flag | n/a | 1x2604 |  | BI2603 |  | 0 | 1 |  |  | Supply temperature sensor short circuit - Zone 17
0x1EB9 | ZoneModule 18 - Window/Frost Value | n/a | 1x2701 |  | BI2700 |  | 0 | 1 |  |  | State on input "Window/Frost" - Zone 17 * Is the input configured as window contact, the window is closed when state is "1" * Is the input configured as frost thermostat, then frostalarm is activ when state is "0"
0x1A66 | ZoneModule 18 - PIR Active Flag | n/a | 1x2702 |  | BI2701 |  | 0 | 1 |  |  | PIR movement sensor activated - Zone 18
0x1A65 | ZoneModule 18 - Room Temp Sensor Short Circuit Flag | n/a | 1x2703 |  | BI2702 |  | 0 | 1 |  |  | Roomtemperatur sensor short circuit - Zone 18
0x1A70 | ZoneModule 18 - Supply Temp Sensor Short Circuit Flag | n/a | 1x2704 |  | BI2703 |  | 0 | 1 |  |  | Supply temperature sensor short circuit - Zone 18
0x1A71 | ZoneModule 19 - Window/Frost Value | n/a | 1x2801 |  | BI2800 |  | 0 | 1 |  |  | State on input "Window/Frost" - Zone 19 * Is the input configured as window contact, the window is closed when state is "1" * Is the input configured as frost thermostat, then frostalarm is activ when state is "0"
0x1A73 | ZoneModule 19 - PIR Active Flag | n/a | 1x2802 |  | BI2801 |  | 0 | 1 |  |  | PIR movement sensor activated - Zone 19
0x1A80 | ZoneModule 19 - Room Temp Sensor Short Circuit Flag | n/a | 1x2803 |  | BI2802 |  | 0 | 1 |  |  | Roomtemperatur sensor short circuit - Zone 19
0x1A81 | ZoneModule 19 - Supply Temp Sensor Short Circuit Flag | n/a | 1x2804 |  | BI2803 |  | 0 | 1 |  |  | Supply temperature sensor short circuit - Zone 19
0x1A82 | ZoneModule 20 - Window/Frost Value | n/a | 1x2901 |  | BI2900 |  | 0 | 1 |  |  | State on input "Window/Frost" - Zone 20 * Is the input configured as window contact, the window is closed when state is "1" * Is the input configured as frost thermostat, then frostalarm is activ when state is "0"
0x1A83 | ZoneModule 20 - PIR Active Flag | n/a | 1x2902 |  | BI2901 |  | 0 | 1 |  |  | PIR movement sensor activated - Zone 20
0x1A84 | ZoneModule 20 - Room Temp Sensor Short Circuit Flag | n/a | 1x2903 |  | BI2902 |  | 0 | 1 |  |  | Roomtemperatur sensor short circuit - Zone 20
0x1A88 | ZoneModule 20 - Supply Temp Sensor Short Circuit Flag | n/a | 1x2904 |  | BI2903 |  | 0 | 1 |  |  | Supply temperature sensor short circuit - Zone 20
0x1A89 | ZoneModule 21 - Window/Frost Value | n/a | 1x3001 |  | BI3000 |  | 0 | 1 |  |  | State on input "Window/Frost" - Zone 21 * Is the input configured as window contact, the window is closed when state is "1" * Is the input configured as frost thermostat, then frostalarm is activ when state is "0"
0x1298 | ZoneModule 21 - PIR Active Flag | n/a | 1x3002 |  | BI3001 |  | 0 | 1 |  |  | PIR movement sensor activated - Zone 21
0x1292 | ZoneModule 21 - Room Temp Sensor Short Circuit Flag | n/a | 1x3003 |  | BI3002 |  | 0 | 1 |  |  | Roomtemperatur sensor short circuit - Zone 21
0x1294 | ZoneModule 21 - Supply Temp Sensor Short Circuit Flag | n/a | 1x3004 |  | BI3003 |  | 0 | 1 |  |  | Supply temperature sensor short circuit - Zone 21
0x1295 | ZoneModule 22 - Window/Frost Value | n/a | 1x3101 |  | BI3100 |  | 0 | 1 |  |  | State on input "Window/Frost" - Zone 22 * Is the input configured as window contact, the window is closed when state is "1" * Is the input configured as frost thermostat, then frostalarm is activ when state is "0"
0x1297 | ZoneModule 22 - PIR Active Flag | n/a | 1x3102 |  | BI3101 |  | 0 | 1 |  |  | PIR movement sensor activated - Zone 22
0x129A | ZoneModule 22 - Room Temp Sensor Short Circuit Flag | n/a | 1x3103 |  | BI3102 |  | 0 | 1 |  |  | Roomtemperatur sensor short circuit - Zone 22
0x1291 | ZoneModule 22 - Supply Temp Sensor Short Circuit Flag | n/a | 1x3104 |  | BI3103 |  | 0 | 1 |  |  | Supply temperature sensor short circuit - Zone 22
0x129C | ZoneModule 23 - Window/Frost Value | n/a | 1x3201 |  | BI3200 |  | 0 | 1 |  |  | State on input "Window/Frost" - Zone 23 * Is the input configured as window contact, the window is closed when state is "1" * Is the input configured as frost thermostat, then frostalarm is activ when state is "0"
0x129D | ZoneModule 23 - PIR Active Flag | n/a | 1x3202 |  | BI3201 |  | 0 | 1 |  |  | PIR movement sensor activated - Zone 23
0x1293 | ZoneModule 23 - Room Temp Sensor Short Circuit Flag | n/a | 1x3203 |  | BI3202 |  | 0 | 1 |  |  | Roomtemperatur sensor short circuit - Zone 23
0x13F0 | ZoneModule 23 - Supply Temp Sensor Short Circuit Flag | n/a | 1x3204 |  | BI3203 |  | 0 | 1 |  |  | Supply temperature sensor short circuit - Zone 23
0x13F2 | ZoneModule 24 - Window/Frost Value | n/a | 1x3301 |  | BI3300 |  | 0 | 1 |  |  | State on input "Window/Frost" - Zone 24 * Is the input configured as window contact, the window is closed when state is "1" * Is the input configured as frost thermostat, then frostalarm is activ when state is "0"
0x1122 | ZoneModule 24 - PIR Active Flag | n/a | 1x3302 |  | BI3301 |  | 0 | 1 |  |  | PIR movement sensor activated - Zone 24
0x1123 | ZoneModule 24 - Room Temp Sensor Short Circuit Flag | n/a | 1x3303 |  | BI3302 |  | 0 | 1 |  |  | Roomtemperatur sensor short circuit - Zone 24
0x1EA0 | ZoneModule 24 - Supply Temp Sensor Short Circuit Flag | n/a | 1x3304 |  | BI3303 |  | 0 | 1 |  |  | Supply temperature sensor short circuit - Zone 24
0x1EA1 | ZoneModule 25 - Window/Frost Value | n/a | 1x3401 |  | BI3400 |  | 0 | 1 |  |  | State on input "Window/Frost" - Zone 25 * Is the input configured as window contact, the window is closed when state is "1" * Is the input configured as frost thermostat, then frostalarm is activ when state is "0"
0x1EA2 | ZoneModule 25 - PIR Active Flag | n/a | 1x3402 |  | BI3401 |  | 0 | 1 |  |  | PIR movement sensor activated - Zone 25
0x1EA3 | ZoneModule 25 - Room Temp Sensor Short Circuit Flag | n/a | 1x3403 |  | BI3402 |  | 0 | 1 |  |  | Roomtemperatur sensor short circuit - Zone 25
0x1E97 | ZoneModule 25 - Supply Temp Sensor Short Circuit Flag | n/a | 1x3404 |  | BI3403 |  | 0 | 1 |  |  | Supply temperature sensor short circuit - Zone 25
| 1. Info |  | Input register (R) |  | Analog input (R) | 1. Info | 1. Info | 1. Info |  |  | 1. Info
0x2030 | AHU Supply Fan Setpoint | % | 3x0101 |  | AI100 |  | 0 | 10000 | Actual supply motor signal setpoint [1/100%] |  | Actual supply motor signal setpoint [1/100%]
0x2162 | AHU Extract Fan Setpoint | % | 3x0102 |  | AI101 |  | 0 | 10000 |  |  | Actual extract motor signal setpoint [1/100%]
0x2163 | AHU Supply Air Temp Setpoint | °C | 3x0103 |  | AI102 |  | -4000 | 10000 |  |  | Actual supplytemperature, calculated setpoint [1/100%]
0x2262 | AHU Cooling Pump Setpoint | % | 3x0104 |  | AI103 |  | 0 | 10000 |  |  | Actual coolingwater tenperature, calculated setpoint [1/100%]
0x2263 | AHU status |  | 3x0105 |  | AI104 |  | 0 | 3 |  |  | Actual operation AHU: 0 = Normal 1 = Stop 2 = Summernight cooling 3 = Fire
0x2140 | AHU Supply Fan Alarm Status |  | 3x0106 |  | AI105 |  | 0 | 1 |  |  | Alarmstate; supply fan [1=Alarm]
0x2141 | AHU Extract Fan Alarm Status |  | 3x0107 |  | AI106 |  | 0 | 1 |  |  | Alarmstate; extract fan [1=Alarm]
0x2240 | AHU Cooling Water Temp Value | °C | 3x0108 |  | AI107 |  | -4000 | 10000 |  |  | Actual coolingwater temperature [1/100%]
0x2241 | AHU Combined Outdoor Temp Value | °C | 3x0109 |  | AI108 |  | -4000 | 10000 |  |  | Actual outdoor temperature [1/100°C]
0x2450 | Section Zone Master Alarm Status |  | 3x0110 |  | AI109 |  | 0 | 2 |  |  | Alarmstate; OJ Green Zone Master [0=no alarm; 1=B-Alarm; 2=A-alarm]
0x2441 | Section Zone Module Alarm Status |  | 3x0111 |  | AI110 |  | 0 | 2 |  |  | Alarmstate; OJ Green Zone Moduler [0=no alarm; 1=B-Alarm; 2=A-alarm]
0x2442 | Zone Master Operation Mode |  | 3x0112 |  | AI111 |  | 0 | 6 |  |  | Actual operation; OJ Green Zone Master:0 - normal, 1 - standby, 2 - summer night cooling, 3 - max air, 4 - min air, 5 - fire, 6 - override
0x2470 | Actual Summer/Winter Compensation |  | 3x0113 |  | AI112 |  | -20000 | 20000 |  |  | Actual status summer / winter compensation [1/100°C]
0x2471 | Number Of Zonemodules |  | 3x0301 |  | AI300 |  | 0 | 25 |  |  | Number of connected OJ Green Zone Modules
0x3141 | Section Supply Fan Max Damper Pos | % | 3x0302 |  | AI301 |  | 0 | 10000 |  |  | Opening position of the VAV supply damper in the section, which is most %-open [1/100%]
0x3241 | Section Extract Fan Max Damper Pos | % | 3x0303 |  | AI302 |  | 0 | 10000 |  |  | Opening position of the VAV extract damper in the section, which is most %-open [1/100%]
0x2100 | Section Heat Valve Max Valve Pos | % | 3x0304 |  | AI303 |  | 0 | 10000 |  |  | Opening position of the heating valve in the section, which is most %-open [1/100%]
0x2101 | Section Cool Valve Max Valve Pos | % | 3x0305 |  | AI304 |  | 0 | 10000 |  |  | Opening position of the cooling valve in the section, which is most %-open [1/100%]
0x2200 | Section Minimum Temperature Setpoint | °C | 3x0306 |  | AI305 |  | -4000 | 10000 |  |  | Actual min. supplytemperature [1/100°C]
0x2201 | Section Cooling Requirement |  | 3x0307 |  | AI306 |  | 0 | 1 |  |  | Cooling requirement in minimum 1 zone
0x2300 | ZoneModule 1 - Status |  | 3x1001 |  | AI1000 |  | 0 | 2 |  |  | Actual status, OJ GreenZone Module 1: 0 = Normal 1 = B-alarm 2 = A-alarm
0x2310 | ZoneModule 1 - VAV Supply 1 Actuator Setpoint % | % | 3x1002 |  | AI1001 |  | 0 | 10000 |  |  | Zone 1; Actual setpoint; VAV inlet damper no. 1 [1/100 %]
| ZoneModule 1 - VAV Supply 1 Actual Flow | m3/h | 3x1003 |  | AI1002 |  | 0 | 65535 |  |  | Zone 1; Actual air quantity;VAV inlet damper no. 1 [m3/h]
| ZoneModule 1 - VAV Supply 2 Actuator Setpoint % | % | 3x1004 |  | AI1003 |  | 0 | 10000 |  |  | Zone 1; Actual setpoint;VAV inlet damper no. 2 [1/100 %]
| ZoneModule 1 - VAV Supply 2 Actual Flow | m3/h | 3x1005 |  | AI1004 |  | 0 | 65535 |  |  | Zone 1; Actual air quantity;VAV inlet damper no. 2 [m3/h]
| ZoneModule 1 - VAV Extract Actuator Setpoint % | % | 3x1006 |  | AI1005 |  | 0 | 10000 |  |  | Zone 1; Actual setpoint;VAV exhaust damper [1/100 %]
| ZoneModule 1 - VAV Extract Actual Flow | m3/h | 3x1007 |  | AI1006 |  | 0 | 65535 |  |  | Zone 1; Actual air quantity; VAV exhaust damper [m3/h]
| ZoneModule 1 - Heating Valve Setpoint % | % | 3x1008 |  | AI1007 |  | 0 | 10000 |  |  | Zone 1; Actual opening, heating valve [1/100 %]
| ZoneModule 1 - Cooling Valve Setpoint % | % | 3x1009 |  | AI1008 |  | 0 | 10000 |  |  | Zone 1; Actual opening, cooling valve [1/100 %]
| ZoneModule 1 - Room Temperature Actual Value | °C | 3x1010 |  | AI1009 |  | -4000 | 10000 |  |  | Zone 1; Actual room temperature [1/100 °C]
| ZoneModule 1 - Supply Temperature Actual Value | °C | 3x1011 |  | AI1010 |  | -4000 | 10000 |  |  | Zone 1; Actual inlet temperature [1/100 °C]
| ZoneModule 1 - Remote Setpoint Offset Actual Value | K | 3x1012 |  | AI1011 |  | -4000 | 10000 |  |  | Zone 1; Actual temperature offset from potentiometer [1/100 °C]
| ZoneModule 1 - CO2/VOC Actual Value | ppm | 3x1013 |  | AI1012 |  | 0 | 5000 |  |  | Zone 1; Actual CO2/VOC level [ppm]
| ZoneModule 1 - RH Actual Value | rh | 3x1014 |  | AI1013 |  | 0 | 10000 |  |  | Zone 1; Actual relative humidity level [%rh]
| ZoneModule 1 - Room Temperature Actual Setpoint | °C | 3x1015 |  | AI1014 |  | -4000 | 10000 |  |  | Zone 1; Actual controller setpoint; room temperature [1/100 °C]
| ZoneModule 1 - Room Panel Air Mode |  | 3x1016 | 3.30 | AI1015 | 3.30 | 0 | 3 |  |  | Zone 1; RPT-20 Room Panel; Actual Air Mode: 0 = Auto 1 = Low 2 = High 3 = Stop
| ZoneModule 1 - Heating Valve Actual Flow | l/h | 3x1017 | 3.30 | AI1016 | 3.30 | 0 | 65535 |  |  | Zone 1; Actual Flow; Heating Valve [l/h]
| ZoneModule 1 - Cooling Valve Actual Flow | l/h | 3x1018 | 3.30 | AI1017 | 3.30 | 0 | 65535 |  |  | Zone 1; Actual Flow; Cooling Valve [l/h]
| ZoneModule 1 - VAV Supply 1 Actual Damper pos. % | % | 3x1019 | 3.30 | AI1018 | 3.30 | 0 | 10000 |  |  | Zone 1; Actual setpoint; VAV Supply 1 damper no. 1 [1/100 %]
| ZoneModule 1 - VAV Supply 2 Actual Damper pos. % | % | 3x1020 | 3.30 | AI1019 | 3.30 | 0 | 10000 |  |  | Zone 1; Actual air quantity;VAV Supply 1 damper no. 1 [m3/h]
| ZoneModule 1 - VAV Extract Actual Damper pos. % | % | 3x1021 | 3.30 | AI1020 | 3.30 | 0 | 10000 |  |  | Zone 1; Actual position; VAV Extract 1 damper no. 1 [1/100 %]
| ZoneModule 1 - EL Heater 1 Temp. Sensor Value | °C | 3x1022 | 3.40 | AI1021 | 3.40 | -4000 | 10000 |  |  | Zone 1; Electric heating Coil 1; Sensor Temperature [1/100 °C]
| ZoneModule 1 - EL Heater 2 Temp. Sensor Value | °C | 3x1023 | 3.40 | AI1022 | 3.40 | -4000 | 10000 |  |  | Zone 1; Electric heating Coil 2; Sensor Temperature [1/100 °C]
| ZoneModule 1 - Ext Aout1 Output | % | 3x1024 | 3.40 | AI1023 | 3.40 | 0 | 10000 |  |  | Zone 1; Extension Module; Actual value Analog Output Aout1 [1/100 V]
| ZoneModule 1 - Ext Aout2 Output | % | 3x1025 | 3.40 | AI1024 | 3.40 | 0 | 10000 |  |  | Zone 1; Extension Module; Actual value Analog Output Aout2 [1/100 V]
| ZoneModule 1 - ZoneModule Alarm Bitmap 1 |  | 3x1026 | 3.40 | AI1025 | 3.40 | 0 | 65535 |  |  | Zone 1; Alarm Bit Map 1 - see tab below: Bit Map Alarm Overview
| ZoneModule 1 - ZoneModule Alarm Bitmap 2 |  | 3x1027 | 3.40 | AI1026 | 3.40 | 0 | 65535 |  |  | Zone 1; Alarm Bit Map 2 - see tab below: Bit Map Alarm Overview
| ZoneModule 1 - ZoneModule Alarm Bitmap 3 |  | 3x1028 | 3.40 | AI1027 | 3.40 | 0 | 65535 |  |  | Zone 1; Alarm Bit Map 3 - see tab below: Bit Map Alarm Overview
| ZoneModule 1 - ZoneModule Alarm Bitmap 4 |  | 3x1029 | 3.40 | AI1028 | 3.40 | 0 | 65535 |  |  | Zone 1; Alarm Bit Map 4 - see tab below: Bit Map Alarm Overview
| ZoneModule 1 - VAV Extract 2 Actuator Setpoint % | % | 3x1030 | 3.40 | AI1029 | 3.40 | 0 | 10000 |  |  | Zone 1; Actual setpoint; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 1 - VAV Extract 2 Actual Flow | m3/h | 3x1031 | 3.40 | AI1030 | 3.40 | 0 | 65535 |  |  | Zone 1; Actual air quantity;VAV Extract 2 damper no. 1 [m3/h]
| ZoneModule 1 - VAV Extract 2 Actual Damper pos. % | % | 3x1032 | 3.40 | AI1031 | 3.40 | 0 | 10000 |  |  | Zone 1; Actual position; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 2 - Status |  | 3x1101 |  | AI1100 |  | 0 | 2 |  |  | Actual status, OJ GreenZone Module 2: 0 = Normal 1 = B-alarm 2 = A-alarm
| ZoneModule 2 - VAV Supply 1 Actuator Setpoint % | % | 3x1102 |  | AI1101 |  | 0 | 10000 |  |  | Zone 2; Actual setpoint;VAV inlet damper no. 1 [1/100 %]
| ZoneModule 2 - VAV Supply 1 Actual Flow | m3/h | 3x1103 |  | AI1102 |  | 0 | 65535 |  |  | Zone 2; Actual air quantity;VAV inlet damper no. 1 [m3/h]
| ZoneModule 2 - VAV Supply 2 Actuator Setpoint % | % | 3x1104 |  | AI1103 |  | 0 | 10000 |  |  | Zone 2; Actual setpoint;VAV inlet damper no. 2 [1/100 %]
| ZoneModule 2 - VAV Supply 2 Actual Flow | m3/h | 3x1105 |  | AI1104 |  | 0 | 65535 |  |  | Zone 2; Actual air quantity; VAV inlet damper no. 2 [m3/h]
| ZoneModule 2 - VAV Extract Actuator Setpoint % | % | 3x1106 |  | AI1105 |  | 0 | 10000 |  |  | Zone 2; Actual setpoint; VAV exhaust damper [1/100 %]
| ZoneModule 2 - VAV Extract Actual Flow | m3/h | 3x1107 |  | AI1106 |  | 0 | 65535 |  |  | Zone 2; Actual air quantity; VAV exhaust damper [m3/h]
| ZoneModule 2 - Heating Valve Setpoint % | % | 3x1108 |  | AI1107 |  | 0 | 10000 |  |  | Zone 2; Actual opening, heating valve [1/100 %]
| ZoneModule 2 - Cooling Valve Setpoint % | % | 3x1109 |  | AI1108 |  | 0 | 10000 |  |  | Zone 2; Actual opening, cooling valve [1/100 %]
| ZoneModule 2 - Room Temperature Actual Value | °C | 3x1110 |  | AI1109 |  | -4000 | 10000 |  |  | Zone 2; Actual room temperature [1/100 °C]
| ZoneModule 2 - Supply Temperature Actual Value | °C | 3x1111 |  | AI1110 |  | -4000 | 10000 |  |  | Zone 2; Actual inlet temperature [1/100 °C]
| ZoneModule 2 - Remote Setpoint Offset Actual Value | K | 3x1112 |  | AI1111 |  | -4000 | 10000 |  |  | Zone 2; Actual temperature offset from potentiometer [1/100 °C]
| ZoneModule 2 - CO2/VOC Actual Value | ppm | 3x1113 |  | AI1112 |  | 0 | 5000 |  |  | Zone 2; Actual CO2/VOC level [ppm]
| ZoneModule 2 - RH Actual Value | rh | 3x1114 |  | AI1113 |  | 0 | 10000 |  |  | Zone 2; Actual relative humidity level [%rh]
| ZoneModule 2 - Room Temperature Actual Setpoint | °C | 3x1115 |  | AI1114 |  | -4000 | 10000 |  |  | Zone 2; Actual controller setpoint, room temperature [1/100 °C]
| ZoneModule 2 - Room Panel Air Mode |  | 3x1116 | 3.30 | AI1115 | 3.30 | 0 | 3 |  |  | Zone 2; RPT-20 Room Panel; Actual Air Mode: 0 = Auto 1 = Low 2 = High 3 = Stop
| ZoneModule 2 - Heating Valve Actual Flow | l/h | 3x1117 | 3.30 | AI1116 | 3.30 | 0 | 65535 |  |  | Zone 2; Actual Flow; Heating Valve [l/h]
| ZoneModule 2 - Cooling Valve Actual Flow | l/h | 3x1118 | 3.30 | AI1117 | 3.30 | 0 | 65535 |  |  | Zone 2; Actual Flow; Cooling Valve [l/h]
| ZoneModule 2 - VAV Supply 1 Actual Damper pos. % | % | 3x1119 | 3.30 | AI1118 | 3.30 | 0 | 10000 |  |  | Zone 2; Actual setpoint; VAV Supply 1 damper no. 1 [1/100 %]
| ZoneModule 2 - VAV Supply 2 Actual Damper pos. % | % | 3x1120 | 3.30 | AI1119 | 3.30 | 0 | 10000 |  |  | Zone 2; Actual air quantity;VAV Supply 1 damper no. 1 [m3/h]
| ZoneModule 2 - VAV Extract Actual Damper pos. % | % | 3x1121 | 3.30 | AI1120 | 3.30 | 0 | 10000 |  |  | Zone 2; Actual position; VAV Extract 1 damper no. 1 [1/100 %]
| ZoneModule 2 - EL Heater 1 Temp. Sensor Value | °C | 3x1122 | 3.40 | AI1121 | 3.40 | -4000 | 10000 |  |  | Zone 2; Electric heating Coil 1; Sensor Temperature [1/100 °C]
| ZoneModule 2 - EL Heater 2 Temp. Sensor Value | °C | 3x1123 | 3.40 | AI1122 | 3.40 | -4000 | 10000 |  |  | Zone 2; Electric heating Coil 2; Sensor Temperature [1/100 °C]
| ZoneModule 2 - Ext Aout1 Output | % | 3x1124 | 3.40 | AI1123 | 3.40 | 0 | 10000 |  |  | Zone 2; Extension Module; Actual value Analog Output Aout1 [1/100 V]
| ZoneModule 2 - Ext Aout2 Output | % | 3x1125 | 3.40 | AI1124 | 3.40 | 0 | 10000 |  |  | Zone 2; Extension Module; Actual value Analog Output Aout2 [1/100 V]
| ZoneModule 2 - ZoneModule Alarm Bitmap 1 |  | 3x1126 | 3.40 | AI1125 | 3.40 | 0 | 65535 |  |  | Zone 2; Alarm Bit Map 1 - see tab below: Bit Map Alarm Overview
| ZoneModule 2 - ZoneModule Alarm Bitmap 2 |  | 3x1127 | 3.40 | AI1126 | 3.40 | 0 | 65535 |  |  | Zone 2; Alarm Bit Map 2 - see tab below: Bit Map Alarm Overview
| ZoneModule 2 - ZoneModule Alarm Bitmap 3 |  | 3x1128 | 3.40 | AI1127 | 3.40 | 0 | 65535 |  |  | Zone 2; Alarm Bit Map 3 - see tab below: Bit Map Alarm Overview
| ZoneModule 2 - ZoneModule Alarm Bitmap 4 |  | 3x1129 | 3.40 | AI1128 | 3.40 | 0 | 65535 |  |  | Zone 2; Alarm Bit Map 4 - see tab below: Bit Map Alarm Overview
| ZoneModule 2 - VAV Extract 2 Actuator Setpoint % | % | 3x1130 | 3.40 | AI1129 | 3.40 | 0 | 10000 |  |  | Zone 2; Actual setpoint; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 2 - VAV Extract 2 Actual Flow | m3/h | 3x1131 | 3.40 | AI1130 | 3.40 | 0 | 65535 |  |  | Zone 2; Actual air quantity;VAV Extract 2 damper no. 1 [m3/h]
| ZoneModule 2 - VAV Extract 2 Actual Damper pos. % | % | 3x1132 | 3.40 | AI1131 | 3.40 | 0 | 10000 |  |  | Zone 2; Actual position; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 3 - Status |  | 3x1201 |  | AI1200 |  | 0 | 2 |  |  | Actual status, OJ GreenZone Module 3: 0 = Normal 1 = B-alarm 2 = A-alarm
| ZoneModule 3 - VAV Supply 1 Actuator Setpoint % | % | 3x1202 |  | AI1201 |  | 0 | 10000 |  |  | Zone 3; Actual setpoint; VAV inlet damper no. 1 [1/100 %]
| ZoneModule 3 - VAV Supply 1 Actual Flow | m3/h | 3x1203 |  | AI1202 |  | 0 | 65535 |  |  | Zone 3; Actual air quantity; VAV inlet damper no. 1 [m3/h]
| ZoneModule 3 - VAV Supply 2 Actuator Setpoint % | % | 3x1204 |  | AI1203 |  | 0 | 10000 |  |  | Zone 3; Actual setpoint; VAV inlet damper no. 2 [1/100 %]
| ZoneModule 3 - VAV Supply 2 Actual Flow | m3/h | 3x1205 |  | AI1204 |  | 0 | 65535 |  |  | Zone 3; Actual air quantity; VAV inlet damper no. 2 [m3/h]
| ZoneModule 3 - VAV Extract Actuator Setpoint % | % | 3x1206 |  | AI1205 |  | 0 | 10000 |  |  | Zone 3; Actual setpoint; VAV exhaust damper [1/100 %]
| ZoneModule 3 - VAV Extract Actual Flow | m3/h | 3x1207 |  | AI1206 |  | 0 | 65535 |  |  | Zone 3; Actual air quantity; VAV exhaust damper [m3/h]
| ZoneModule 3 - Heating Valve Setpoint % | % | 3x1208 |  | AI1207 |  | 0 | 10000 |  |  | Zone 3; Actual opening, heating valve [1/100 %]
| ZoneModule 3 - Cooling Valve Setpoint % | % | 3x1209 |  | AI1208 |  | 0 | 10000 |  |  | Zone 3; Actual opening, cooling valve [1/100 %]
| ZoneModule 3 - Room Temperature Actual Value | °C | 3x1210 |  | AI1209 |  | -4000 | 10000 |  |  | Zone 3; Actual room temperature [1/100 °C]
| ZoneModule 3 - Supply Temperature Actual Value | °C | 3x1211 |  | AI1210 |  | -4000 | 10000 |  |  | Zone 3; Actual inlet temperature [1/100 °C]
| ZoneModule 3 - Remote Setpoint Offset Actual Value | K | 3x1212 |  | AI1211 |  | -4000 | 10000 |  |  | Zone 3; Actual temperature offset from potentiometer [1/100 °C]
| ZoneModule 3 - CO2/VOC Actual Value | ppm | 3x1213 |  | AI1212 |  | 0 | 5000 |  |  | Zone 3; Actual CO2/VOC level [ppm]
| ZoneModule 3 - RH Actual Value | rh | 3x1214 |  | AI1213 |  | 0 | 10000 |  |  | Zone 3; Actual relative humidity level [%rh]
| ZoneModule 3 - Room Temperature Actual Setpoint | °C | 3x1215 |  | AI1214 |  | -4000 | 10000 |  |  | Zone 3; Actual controller setpoint, room temperature [1/100 °C]
| ZoneModule 3 - Room Panel Air Mode |  | 3x1216 | 3.30 | AI1215 | 3.30 | 0 | 3 |  |  | Zone 3; RPT-20 Room Panel; Actual Air Mode: 0 = Auto 1 = Low 2 = High 3 = Stop
| ZoneModule 3 - Heating Valve Actual Flow | l/h | 3x1217 | 3.30 | AI1216 | 3.30 | 0 | 65535 |  |  | Zone 3; Actual Flow; Heating Valve [l/h]
| ZoneModule 3 - Cooling Valve Actual Flow | l/h | 3x1218 | 3.30 | AI1217 | 3.30 | 0 | 65535 |  |  | Zone 3; Actual Flow; Cooling Valve [l/h]
| ZoneModule 3 - VAV Supply 1 Actual Damper pos. % | % | 3x1219 | 3.30 | AI1218 | 3.30 | 0 | 10000 |  |  | Zone 3; Actual setpoint; VAV Supply 1 damper no. 1 [1/100 %]
| ZoneModule 3 - VAV Supply 2 Actual Damper pos. % | % | 3x1220 | 3.30 | AI1219 | 3.30 | 0 | 10000 |  |  | Zone 3; Actual air quantity;VAV Supply 1 damper no. 1 [m3/h]
| ZoneModule 3 - VAV Extract Actual Damper pos. % | % | 3x1221 | 3.30 | AI1220 | 3.30 | 0 | 10000 |  |  | Zone 3; Actual position; VAV Extract 1 damper no. 1 [1/100 %]
| ZoneModule 3 - EL Heater 1 Temp. Sensor Value | °C | 3x1222 | 3.40 | AI1221 | 3.40 | -4000 | 10000 |  |  | Zone 3; Electric heating Coil 1; Sensor Temperature [1/100 °C]
| ZoneModule 3 - EL Heater 2 Temp. Sensor Value | °C | 3x1223 | 3.40 | AI1222 | 3.40 | -4000 | 10000 |  |  | Zone 3; Electric heating Coil 2; Sensor Temperature [1/100 °C]
| ZoneModule 3 - Ext Aout1 Output | % | 3x1224 | 3.40 | AI1223 | 3.40 | 0 | 10000 |  |  | Zone 3; Extension Module; Actual value Analog Output Aout1 [1/100 V]
| ZoneModule 3 - Ext Aout2 Output | % | 3x1225 | 3.40 | AI1224 | 3.40 | 0 | 10000 |  |  | Zone 3; Extension Module; Actual value Analog Output Aout2 [1/100 V]
| ZoneModule 3 - ZoneModule Alarm Bitmap 1 |  | 3x1226 | 3.40 | AI1225 | 3.40 | 0 | 65535 |  |  | Zone 3; Alarm Bit Map 1 - see tab below: Bit Map Alarm Overview
| ZoneModule 3 - ZoneModule Alarm Bitmap 2 |  | 3x1227 | 3.40 | AI1226 | 3.40 | 0 | 65535 |  |  | Zone 3; Alarm Bit Map 2 - see tab below: Bit Map Alarm Overview
| ZoneModule 3 - ZoneModule Alarm Bitmap 3 |  | 3x1228 | 3.40 | AI1227 | 3.40 | 0 | 65535 |  |  | Zone 3; Alarm Bit Map 3 - see tab below: Bit Map Alarm Overview
| ZoneModule 3 - ZoneModule Alarm Bitmap 4 |  | 3x1229 | 3.40 | AI1228 | 3.40 | 0 | 65535 |  |  | Zone 3; Alarm Bit Map 4 - see tab below: Bit Map Alarm Overview
| ZoneModule 3 - VAV Extract 2 Actuator Setpoint % | % | 3x1230 | 3.40 | AI1229 | 3.40 | 0 | 10000 |  |  | Zone 3; Actual setpoint; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 3 - VAV Extract 2 Actual Flow | m3/h | 3x1231 | 3.40 | AI1230 | 3.40 | 0 | 65535 |  |  | Zone 3; Actual air quantity;VAV Extract 2 damper no. 1 [m3/h]
| ZoneModule 3 - VAV Extract 2 Actual Damper pos. % | % | 3x1232 | 3.40 | AI1231 | 3.40 | 0 | 10000 |  |  | Zone 3; Actual position; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 4 - Status |  | 3x1301 |  | AI1300 |  | 0 | 2 |  |  | Actual status, OJ GreenZone Module 4: 0 = Normal 1 = B-alarm 2 = A-alarm
| ZoneModule 4 - VAV Supply 1 Actuator Setpoint % | % | 3x1302 |  | AI1301 |  | 0 | 10000 |  |  | Zone 4; Actual setpoint; VAV inlet damper no. 1 [1/100 %]
| ZoneModule 4 - VAV Supply 1 Actual Flow | m3/h | 3x1303 |  | AI1302 |  | 0 | 65535 |  |  | Zone 4; Actual air quantity; VAV inlet damper no. 1 [m3/h]
| ZoneModule 4 - VAV Supply 2 Actuator Setpoint % | % | 3x1304 |  | AI1303 |  | 0 | 10000 |  |  | Zone 4; Actual setpoint; VAV inlet damper no. 2 [1/100 %]
| ZoneModule 4 - VAV Supply 2 Actual Flow | m3/h | 3x1305 |  | AI1304 |  | 0 | 65535 |  |  | Zone 4; Actual air quantity; VAV inlet damper no. 2 [m3/h]
| ZoneModule 4 - VAV Extract Actuator Setpoint % | % | 3x1306 |  | AI1305 |  | 0 | 10000 |  |  | Zone 4; Actual setpoint; VAV exhaust damper [1/100 %]
| ZoneModule 4 - VAV Extract Actual Flow | m3/h | 3x1307 |  | AI1306 |  | 0 | 65535 |  |  | Zone 4; Actual air quantity; VAV exhaust damper [m3/h]
| ZoneModule 4 - Heating Valve Setpoint % | % | 3x1308 |  | AI1307 |  | 0 | 10000 |  |  | Zone 4; Actual opening, heating valve [1/100 %]
| ZoneModule 4 - Cooling Valve Setpoint % | % | 3x1309 |  | AI1308 |  | 0 | 10000 |  |  | Zone 4; Actual opening, cooling valve [1/100 %]
| ZoneModule 4 - Room Temperature Actual Value | °C | 3x1310 |  | AI1309 |  | -4000 | 10000 |  |  | Zone 4; Actual room temperature [1/100 °C]
| ZoneModule 4 - Supply Temperature Actual Value | °C | 3x1311 |  | AI1310 |  | -4000 | 10000 |  |  | Zone 4; Actual inlet temperature [1/100 °C]
| ZoneModule 4 - Remote Setpoint Offset Actual Value | K | 3x1312 |  | AI1311 |  | -4000 | 10000 |  |  | Zone 4; Actual temperature offset from potentiometer [1/100 °C]
| ZoneModule 4 - CO2/VOC Actual Value | ppm | 3x1313 |  | AI1312 |  | 0 | 5000 |  |  | Zone 4; Actual CO2/VOC level [ppm]
| ZoneModule 4 - RH Actual Value | rh | 3x1314 |  | AI1313 |  | 0 | 10000 |  |  | Zone 4; Actual relative humidity level [%rh]
| ZoneModule 4 - Room Temperature Actual Setpoint | °C | 3x1315 |  | AI1314 |  | -4000 | 10000 |  |  | Zone 4; Actual controller setpoint, room temperature [1/100 °C]
| ZoneModule 4 - Room Panel Air Mode |  | 3x1316 | 3.30 | AI1315 | 3.30 | 0 | 3 |  |  | Zone 4; RPT-20 Room Panel; Actual Air Mode: 0 = Auto 1 = Low 2 = High 3 = Stop
| ZoneModule 4 - Heating Valve Actual Flow | l/h | 3x1317 | 3.30 | AI1316 | 3.30 | 0 | 65535 |  |  | Zone 4; Actual Flow; Heating Valve [l/h]
| ZoneModule 4 - Cooling Valve Actual Flow | l/h | 3x1318 | 3.30 | AI1317 | 3.30 | 0 | 65535 |  |  | Zone 4; Actual Flow; Cooling Valve [l/h]
| ZoneModule 4 - VAV Supply 1 Actual Damper pos. % | % | 3x1319 | 3.30 | AI1318 | 3.30 | 0 | 10000 |  |  | Zone 4; Actual setpoint; VAV Supply 1 damper no. 1 [1/100 %]
| ZoneModule 4 - VAV Supply 2 Actual Damper pos. % | % | 3x1320 | 3.30 | AI1319 | 3.30 | 0 | 10000 |  |  | Zone 4; Actual air quantity;VAV Supply 1 damper no. 1 [m3/h]
| ZoneModule 4 - VAV Extract Actual Damper pos. % | % | 3x1321 | 3.30 | AI1320 | 3.30 | 0 | 10000 |  |  | Zone 4; Actual position; VAV Extract 1 damper no. 1 [1/100 %]
| ZoneModule 4 - EL Heater 1 Temp. Sensor Value | °C | 3x1322 | 3.40 | AI1321 | 3.40 | -4000 | 10000 |  |  | Zone 4; Electric heating Coil 1; Sensor Temperature [1/100 °C]
| ZoneModule 4 - EL Heater 2 Temp. Sensor Value | °C | 3x1323 | 3.40 | AI1322 | 3.40 | -4000 | 10000 |  |  | Zone 4; Electric heating Coil 2; Sensor Temperature [1/100 °C]
| ZoneModule 4 - Ext Aout1 Output | % | 3x1324 | 3.40 | AI1323 | 3.40 | 0 | 10000 |  |  | Zone 4; Extension Module; Actual value Analog Output Aout1 [1/100 V]
| ZoneModule 4 - Ext Aout2 Output | % | 3x1325 | 3.40 | AI1324 | 3.40 | 0 | 10000 |  |  | Zone 4; Extension Module; Actual value Analog Output Aout2 [1/100 V]
| ZoneModule 4 - ZoneModule Alarm Bitmap 1 |  | 3x1326 | 3.40 | AI1325 | 3.40 | 0 | 65535 |  |  | Zone 4; Alarm Bit Map 1 - see tab below: Bit Map Alarm Overview
| ZoneModule 4 - ZoneModule Alarm Bitmap 2 |  | 3x1327 | 3.40 | AI1326 | 3.40 | 0 | 65535 |  |  | Zone 4; Alarm Bit Map 2 - see tab below: Bit Map Alarm Overview
| ZoneModule 4 - ZoneModule Alarm Bitmap 3 |  | 3x1328 | 3.40 | AI1327 | 3.40 | 0 | 65535 |  |  | Zone 4; Alarm Bit Map 3 - see tab below: Bit Map Alarm Overview
| ZoneModule 4 - ZoneModule Alarm Bitmap 4 |  | 3x1329 | 3.40 | AI1328 | 3.40 | 0 | 65535 |  |  | Zone 4; Alarm Bit Map 4 - see tab below: Bit Map Alarm Overview
| ZoneModule 4 - VAV Extract 2 Actuator Setpoint % | % | 3x1330 | 3.40 | AI1329 | 3.40 | 0 | 10000 |  |  | Zone 4; Actual setpoint; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 4 - VAV Extract 2 Actual Flow | m3/h | 3x1331 | 3.40 | AI1330 | 3.40 | 0 | 65535 |  |  | Zone 4; Actual air quantity;VAV Extract 2 damper no. 1 [m3/h]
| ZoneModule 4 - VAV Extract 2 Actual Damper pos. % | % | 3x1332 | 3.40 | AI1331 | 3.40 | 0 | 10000 |  |  | Zone 4; Actual position; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 5 - Status |  | 3x1401 |  | AI1400 |  | 0 | 2 |  |  | Actual status, OJ GreenZone Module 5: 0 = Normal 1 = B-alarm 2 = A-alarm
| ZoneModule 5 - VAV Supply 1 Actuator Setpoint % | % | 3x1402 |  | AI1401 |  | 0 | 10000 |  |  | Zone 5; Actual setpoint; VAV inlet damper no. 1 [1/100 %]
| ZoneModule 5 - VAV Supply 1 Actual Flow | m3/h | 3x1403 |  | AI1402 |  | 0 | 65535 |  |  | Zone 5; Actual air quantity; VAV inlet damper no. 1 [m3/h]
| ZoneModule 5 - VAV Supply 2 Actuator Setpoint % | % | 3x1404 |  | AI1403 |  | 0 | 10000 |  |  | Zone 5; Actual setpoint; VAV inlet damper no. 2 [1/100 %]
| ZoneModule 5 - VAV Supply 2 Actual Flow | m3/h | 3x1405 |  | AI1404 |  | 0 | 65535 |  |  | Zone 5; Actual air quantity; VAV inlet damper no. 2 [m3/h]
| ZoneModule 5 - VAV Extract Actuator Setpoint % | % | 3x1406 |  | AI1405 |  | 0 | 10000 |  |  | Zone 5; Actual setpoint; VAV exhaust damper [1/100 %]
| ZoneModule 5 - VAV Extract Actual Flow | m3/h | 3x1407 |  | AI1406 |  | 0 | 65535 |  |  | Zone 5; Actual air quantity; VAV exhaust damper [m3/h]
| ZoneModule 5 - Heating Valve Setpoint % | % | 3x1408 |  | AI1407 |  | 0 | 10000 |  |  | Zone 5; Actual opening, heating valve [1/100 %]
| ZoneModule 5 - Cooling Valve Setpoint % | % | 3x1409 |  | AI1408 |  | 0 | 10000 |  |  | Zone 5; Actual opening, cooling valve [1/100 %]
| ZoneModule 5 - Room Temperature Actual Value | °C | 3x1410 |  | AI1409 |  | -4000 | 10000 |  |  | Zone 5; Actual room temperature [1/100 °C]
| ZoneModule 5 - Supply Temperature Actual Value | °C | 3x1411 |  | AI1410 |  | -4000 | 10000 |  |  | Zone 5; Actual inlet temperature [1/100 °C]
| ZoneModule 5 - Remote Setpoint Offset Actual Value | K | 3x1412 |  | AI1411 |  | -4000 | 10000 |  |  | Zone 5; Actual temperature offset from potentiometer [1/100 °C]
| ZoneModule 5 - CO2/VOC Actual Value | ppm | 3x1413 |  | AI1412 |  | 0 | 5000 |  |  | Zone 5; Actual CO2/VOC level [ppm]
| ZoneModule 5 - RH Actual Value | rh | 3x1414 |  | AI1413 |  | 0 | 10000 |  |  | Zone 5; Actual relative humidity level [%rh]
| ZoneModule 5 - Room Temperature Actual Setpoint | °C | 3x1415 |  | AI1414 |  | -4000 | 10000 |  |  | Zone 5; Actual controller setpoint, room temperature [1/100 °C]
| ZoneModule 5 - Room Panel Air Mode |  | 3x1416 | 3.30 | AI1415 | 3.30 | 0 | 3 |  |  | Zone 5; RPT-20 Room Panel; Actual Air Mode: 0 = Auto 1 = Low 2 = High 3 = Stop
| ZoneModule 5 - Heating Valve Actual Flow | l/h | 3x1417 | 3.30 | AI1416 | 3.30 | 0 | 65535 |  |  | Zone 5; Actual Flow; Heating Valve [l/h]
| ZoneModule 5 - Cooling Valve Actual Flow | l/h | 3x1418 | 3.30 | AI1417 | 3.30 | 0 | 65535 |  |  | Zone 5; Actual Flow; Cooling Valve [l/h]
| ZoneModule 5 - VAV Supply 1 Actual Damper pos. % | % | 3x1419 | 3.30 | AI1418 | 3.30 | 0 | 10000 |  |  | Zone 5; Actual setpoint; VAV Supply 1 damper no. 1 [1/100 %]
| ZoneModule 5 - VAV Supply 2 Actual Damper pos. % | % | 3x1420 | 3.30 | AI1419 | 3.30 | 0 | 10000 |  |  | Zone 5; Actual air quantity;VAV Supply 1 damper no. 1 [m3/h]
| ZoneModule 5 - VAV Extract Actual Damper pos. % | % | 3x1421 | 3.30 | AI1420 | 3.30 | 0 | 10000 |  |  | Zone 5; Actual position; VAV Extract 1 damper no. 1 [1/100 %]
| ZoneModule 5 - EL Heater 1 Temp. Sensor Value | °C | 3x1422 | 3.40 | AI1421 | 3.40 | -4000 | 10000 |  |  | Zone 5; Electric heating Coil 1; Sensor Temperature [1/100 °C]
| ZoneModule 5 - EL Heater 2 Temp. Sensor Value | °C | 3x1423 | 3.40 | AI1422 | 3.40 | -4000 | 10000 |  |  | Zone 5; Electric heating Coil 2; Sensor Temperature [1/100 °C]
| ZoneModule 5 - Ext Aout1 Output | % | 3x1424 | 3.40 | AI1423 | 3.40 | 0 | 10000 |  |  | Zone 5; Extension Module; Actual value Analog Output Aout1 [1/100 V]
| ZoneModule 5 - Ext Aout2 Output | % | 3x1425 | 3.40 | AI1424 | 3.40 | 0 | 10000 |  |  | Zone 5; Extension Module; Actual value Analog Output Aout2 [1/100 V]
| ZoneModule 5 - ZoneModule Alarm Bitmap 1 |  | 3x1426 | 3.40 | AI1425 | 3.40 | 0 | 65535 |  |  | Zone 5; Alarm Bit Map 1 - see tab below: Bit Map Alarm Overview
| ZoneModule 5 - ZoneModule Alarm Bitmap 2 |  | 3x1427 | 3.40 | AI1426 | 3.40 | 0 | 65535 |  |  | Zone 5; Alarm Bit Map 2 - see tab below: Bit Map Alarm Overview
| ZoneModule 5 - ZoneModule Alarm Bitmap 3 |  | 3x1428 | 3.40 | AI1427 | 3.40 | 0 | 65535 |  |  | Zone 5; Alarm Bit Map 3 - see tab below: Bit Map Alarm Overview
| ZoneModule 5 - ZoneModule Alarm Bitmap 4 |  | 3x1429 | 3.40 | AI1428 | 3.40 | 0 | 65535 |  |  | Zone 5; Alarm Bit Map 4 - see tab below: Bit Map Alarm Overview
| ZoneModule 5 - VAV Extract 2 Actuator Setpoint % | % | 3x1430 | 3.40 | AI1429 | 3.40 | 0 | 10000 |  |  | Zone 5; Actual setpoint; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 5 - VAV Extract 2 Actual Flow | m3/h | 3x1431 | 3.40 | AI1430 | 3.40 | 0 | 65535 |  |  | Zone 5; Actual air quantity;VAV Extract 2 damper no. 1 [m3/h]
| ZoneModule 5 - VAV Extract 2 Actual Damper pos. % | % | 3x1432 | 3.40 | AI1431 | 3.40 | 0 | 10000 |  |  | Zone 5; Actual position; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 6 - Status |  | 3x1501 |  | AI1500 |  | 0 | 2 |  |  | Actual status, Zone 6: 0 = Normal 1 = B-alarm 2 = A-alarm
| ZoneModule 6 - VAV Supply 1 Actuator Setpoint % | % | 3x1502 |  | AI1501 |  | 0 | 10000 |  |  | Zone 6; Actual setpoint; VAV inlet damper no. 1 [1/100 %]
| ZoneModule 6 - VAV Supply 1 Actual Flow | m3/h | 3x1503 |  | AI1502 |  | 0 | 65535 |  |  | Zone 6; Actual air quantity; VAV inlet damper no. 1 [m3/h]
| ZoneModule 6 - VAV Supply 2 Actuator Setpoint % | % | 3x1504 |  | AI1503 |  | 0 | 10000 |  |  | Zone 6; Actual setpoint; VAV inlet damper no. 2 [1/100 %]
| ZoneModule 6 - VAV Supply 2 Actual Flow | m3/h | 3x1505 |  | AI1504 |  | 0 | 65535 |  |  | Zone 6; Actual air quantity; VAV inlet damper no. 2 [m3/h]
| ZoneModule 6 - VAV Extract Actuator Setpoint % | % | 3x1506 |  | AI1505 |  | 0 | 10000 |  |  | Zone 6; Actual setpoint; VAV exhaust damper [1/100 %]
| ZoneModule 6 - VAV Extract Actual Flow | m3/h | 3x1507 |  | AI1506 |  | 0 | 65535 |  |  | Zone 6; Actual air quantity; VAV exhaust damper [m3/h]
| ZoneModule 6 - Heating Valve Setpoint % | % | 3x1508 |  | AI1507 |  | 0 | 10000 |  |  | Zone 6; Actual opening, heating valve [1/100 %]
| ZoneModule 6 - Cooling Valve Setpoint % | % | 3x1509 |  | AI1508 |  | 0 | 10000 |  |  | Zone 6; Actual opening, cooling valve [1/100 %]
| ZoneModule 6 - Room Temperature Actual Value | °C | 3x1510 |  | AI1509 |  | -4000 | 10000 |  |  | Zone 6; Actual room temperature [1/100 °C]
| ZoneModule 6 - Supply Temperature Actual Value | °C | 3x1511 |  | AI1510 |  | -4000 | 10000 |  |  | Zone 6; Actual inlet temperature [1/100 °C]
| ZoneModule 6 - Remote Setpoint Offset Actual Value | K | 3x1512 |  | AI1511 |  | -4000 | 10000 |  |  | Zone 6; Actual temperature offset from potentiometer [1/100 °C]
| ZoneModule 6 - CO2/VOC Actual Value | ppm | 3x1513 |  | AI1512 |  | 0 | 5000 |  |  | Zone 6; Actual CO2/VOC level [ppm]
| ZoneModule 6 - RH Actual Value | rh | 3x1514 |  | AI1513 |  | 0 | 10000 |  |  | Zone 6; Actual relative humidity level [%rh]
| ZoneModule 6 - Room Temperature Actual Setpoint | °C | 3x1515 |  | AI1514 |  | -4000 | 10000 |  |  | Zone 6; Actual controller setpoint, room temperature [1/100 °C]
| ZoneModule 6 - Room Panel Air Mode |  | 3x1516 | 3.30 | AI1515 | 3.30 | 0 | 3 |  |  | Zone 6; RPT-20 Room Panel; Actual Air Mode: 0 = Auto 1 = Low 2 = High 3 = Stop
| ZoneModule 6 - Heating Valve Actual Flow | l/h | 3x1517 | 3.30 | AI1516 | 3.30 | 0 | 65535 |  |  | Zone 6; Actual Flow; Heating Valve [l/h]
| ZoneModule 6 - Cooling Valve Actual Flow | l/h | 3x1518 | 3.30 | AI1517 | 3.30 | 0 | 65535 |  |  | Zone 6; Actual Flow; Cooling Valve [l/h]
| ZoneModule 6 - VAV Supply 1 Actual Damper pos. % | % | 3x1519 | 3.30 | AI1518 | 3.30 | 0 | 10000 |  |  | Zone 6; Actual setpoint; VAV Supply 1 damper no. 1 [1/100 %]
| ZoneModule 6 - VAV Supply 2 Actual Damper pos. % | % | 3x1520 | 3.30 | AI1519 | 3.30 | 0 | 10000 |  |  | Zone 6; Actual air quantity;VAV Supply 1 damper no. 1 [m3/h]
| ZoneModule 6 - VAV Extract Actual Damper pos. % | % | 3x1521 | 3.30 | AI1520 | 3.30 | 0 | 10000 |  |  | Zone 6; Actual position; VAV Extract 1 damper no. 1 [1/100 %]
| ZoneModule 6 - EL Heater 1 Temp. Sensor Value | °C | 3x1522 | 3.40 | AI1521 | 3.40 | -4000 | 10000 |  |  | Zone 6; Electric heating Coil 1; Sensor Temperature [1/100 °C]
| ZoneModule 6 - EL Heater 2 Temp. Sensor Value | °C | 3x1523 | 3.40 | AI1522 | 3.40 | -4000 | 10000 |  |  | Zone 6; Electric heating Coil 2; Sensor Temperature [1/100 °C]
| ZoneModule 6 - Ext Aout1 Output | % | 3x1524 | 3.40 | AI1523 | 3.40 | 0 | 10000 |  |  | Zone 6; Extension Module; Actual value Analog Output Aout1 [1/100 V]
| ZoneModule 6 - Ext Aout2 Output | % | 3x1525 | 3.40 | AI1524 | 3.40 | 0 | 10000 |  |  | Zone 6; Extension Module; Actual value Analog Output Aout2 [1/100 V]
| ZoneModule 6 - ZoneModule Alarm Bitmap 1 |  | 3x1526 | 3.40 | AI1525 | 3.40 | 0 | 65535 |  |  | Zone 6; Alarm Bit Map 1 - see tab below: Bit Map Alarm Overview
| ZoneModule 6 - ZoneModule Alarm Bitmap 2 |  | 3x1527 | 3.40 | AI1526 | 3.40 | 0 | 65535 |  |  | Zone 6; Alarm Bit Map 2 - see tab below: Bit Map Alarm Overview
| ZoneModule 6 - ZoneModule Alarm Bitmap 3 |  | 3x1528 | 3.40 | AI1527 | 3.40 | 0 | 65535 |  |  | Zone 6; Alarm Bit Map 3 - see tab below: Bit Map Alarm Overview
| ZoneModule 6 - ZoneModule Alarm Bitmap 4 |  | 3x1529 | 3.40 | AI1528 | 3.40 | 0 | 65535 |  |  | Zone 6; Alarm Bit Map 4 - see tab below: Bit Map Alarm Overview
| ZoneModule 6 - VAV Extract 2 Actuator Setpoint % | % | 3x1530 | 3.40 | AI1529 | 3.40 | 0 | 10000 |  |  | Zone 6; Actual setpoint; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 6 - VAV Extract 2 Actual Flow | m3/h | 3x1531 | 3.40 | AI1530 | 3.40 | 0 | 65535 |  |  | Zone 6; Actual air quantity;VAV Extract 2 damper no. 1 [m3/h]
| ZoneModule 6 - VAV Extract 2 Actual Damper pos. % | % | 3x1532 | 3.40 | AI1531 | 3.40 | 0 | 10000 |  |  | Zone 6; Actual position; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 7 - Status |  | 3x1601 |  | AI1600 |  | 0 | 2 |  |  | Actual status, Zone 7: 0 = Normal 1 = B-alarm 2 = A-alarm
| ZoneModule 7 - VAV Supply 1 Actuator Setpoint % | % | 3x1602 |  | AI1601 |  | 0 | 10000 |  |  | Zone 7; Actual setpoint; VAV inlet damper no. 1 [1/100 %]
| ZoneModule 7 - VAV Supply 1 Actual Flow | m3/h | 3x1603 |  | AI1602 |  | 0 | 65535 |  |  | Zone 7; Actual air quantity; VAV inlet damper no. 1 [m3/h]
| ZoneModule 7 - VAV Supply 2 Actuator Setpoint % | % | 3x1604 |  | AI1603 |  | 0 | 10000 |  |  | Zone 7; Actual setpoint; VAV inlet damper no. 2 [1/100 %]
| ZoneModule 7 - VAV Supply 2 Actual Flow | m3/h | 3x1605 |  | AI1604 |  | 0 | 65535 |  |  | Zone 7; Actual air quantity; VAV inlet damper no. 2 [m3/h]
| ZoneModule 7 - VAV Extract Actuator Setpoint % | % | 3x1606 |  | AI1605 |  | 0 | 10000 |  |  | Zone 7; Actual setpoint; VAV exhaust damper [1/100 %]
| ZoneModule 7 - VAV Extract Actual Flow | m3/h | 3x1607 |  | AI1606 |  | 0 | 65535 |  |  | Zone 7; Actual air quantity; VAV exhaust damper [m3/h]
| ZoneModule 7 - Heating Valve Setpoint % | % | 3x1608 |  | AI1607 |  | 0 | 10000 |  |  | Zone 7; Actual opening, heating valve [1/100 %]
| ZoneModule 7 - Cooling Valve Setpoint % | % | 3x1609 |  | AI1608 |  | 0 | 10000 |  |  | Zone 7; Actual opening, cooling valve [1/100 %]
| ZoneModule 7 - Room Temperature Actual Value | °C | 3x1610 |  | AI1609 |  | -4000 | 10000 |  |  | Zone 7; Actual room temperature [1/100 °C]
| ZoneModule 7 - Supply Temperature Actual Value | °C | 3x1611 |  | AI1610 |  | -4000 | 10000 |  |  | Zone 7; Actual inlet temperature [1/100 °C]
| ZoneModule 7 - Remote Setpoint Offset Actual Value | K | 3x1612 |  | AI1611 |  | -4000 | 10000 |  |  | Zone 7; Actual temperature offset from potentiometer [1/100 °C]
| ZoneModule 7 - CO2/VOC Actual Value | ppm | 3x1613 |  | AI1612 |  | 0 | 5000 |  |  | Zone 7; Actual CO2/VOC level [ppm]
| ZoneModule 7 - RH Actual Value | rh | 3x1614 |  | AI1613 |  | 0 | 10000 |  |  | Zone 7; Actual relative humidity level [%rh]
| ZoneModule 7 - Room Temperature Actual Setpoint | °C | 3x1615 |  | AI1614 |  | -4000 | 10000 |  |  | Zone 7; Actual controller setpoint, room temperature [1/100 °C]
| ZoneModule 7 - Room Panel Air Mode |  | 3x1616 | 3.30 | AI1615 | 3.30 | 0 | 3 |  |  | Zone 7; RPT-20 Room Panel; Actual Air Mode: 0 = Auto 1 = Low 2 = High 3 = Stop
| ZoneModule 7 - Heating Valve Actual Flow | l/h | 3x1617 | 3.30 | AI1616 | 3.30 | 0 | 65535 |  |  | Zone 7; Actual Flow; Heating Valve [l/h]
| ZoneModule 7 - Cooling Valve Actual Flow | l/h | 3x1618 | 3.30 | AI1617 | 3.30 | 0 | 65535 |  |  | Zone 7; Actual Flow; Cooling Valve [l/h]
| ZoneModule 7 - VAV Supply 1 Actual Damper pos. % | % | 3x1619 | 3.30 | AI1618 | 3.30 | 0 | 10000 |  |  | Zone 7; Actual setpoint; VAV Supply 1 damper no. 1 [1/100 %]
| ZoneModule 7 - VAV Supply 2 Actual Damper pos. % | % | 3x1620 | 3.30 | AI1619 | 3.30 | 0 | 10000 |  |  | Zone 7; Actual air quantity;VAV Supply 1 damper no. 1 [m3/h]
| ZoneModule 7 - VAV Extract Actual Damper pos. % | % | 3x1621 | 3.30 | AI1620 | 3.30 | 0 | 10000 |  |  | Zone 7; Actual position; VAV Extract 1 damper no. 1 [1/100 %]
| ZoneModule 7 - EL Heater 1 Temp. Sensor Value | °C | 3x1622 | 3.40 | AI1621 | 3.40 | -4000 | 10000 |  |  | Zone 7; Electric heating Coil 1; Sensor Temperature [1/100 °C]
| ZoneModule 7 - EL Heater 2 Temp. Sensor Value | °C | 3x1623 | 3.40 | AI1622 | 3.40 | -4000 | 10000 |  |  | Zone 7; Electric heating Coil 2; Sensor Temperature [1/100 °C]
| ZoneModule 7 - Ext Aout1 Output | % | 3x1624 | 3.40 | AI1623 | 3.40 | 0 | 10000 |  |  | Zone 7; Extension Module; Actual value Analog Output Aout1 [1/100 V]
| ZoneModule 7 - Ext Aout2 Output | % | 3x1625 | 3.40 | AI1624 | 3.40 | 0 | 10000 |  |  | Zone 7; Extension Module; Actual value Analog Output Aout2 [1/100 V]
| ZoneModule 7 - ZoneModule Alarm Bitmap 1 |  | 3x1626 | 3.40 | AI1625 | 3.40 | 0 | 65535 |  |  | Zone 7; Alarm Bit Map 1 - see tab below: Bit Map Alarm Overview
| ZoneModule 7 - ZoneModule Alarm Bitmap 2 |  | 3x1627 | 3.40 | AI1626 | 3.40 | 0 | 65535 |  |  | Zone 7; Alarm Bit Map 2 - see tab below: Bit Map Alarm Overview
| ZoneModule 7 - ZoneModule Alarm Bitmap 3 |  | 3x1628 | 3.40 | AI1627 | 3.40 | 0 | 65535 |  |  | Zone 7; Alarm Bit Map 3 - see tab below: Bit Map Alarm Overview
| ZoneModule 7 - ZoneModule Alarm Bitmap 4 |  | 3x1629 | 3.40 | AI1628 | 3.40 | 0 | 65535 |  |  | Zone 7; Alarm Bit Map 4 - see tab below: Bit Map Alarm Overview
| ZoneModule 7 - VAV Extract 2 Actuator Setpoint % | % | 3x1630 | 3.40 | AI1629 | 3.40 | 0 | 10000 |  |  | Zone 7; Actual setpoint; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 7 - VAV Extract 2 Actual Flow | m3/h | 3x1631 | 3.40 | AI1630 | 3.40 | 0 | 65535 |  |  | Zone 7; Actual air quantity;VAV Extract 2 damper no. 1 [m3/h]
| ZoneModule 7 - VAV Extract 2 Actual Damper pos. % | % | 3x1632 | 3.40 | AI1631 | 3.40 | 0 | 10000 |  |  | Zone 7; Actual position; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 8 - Status |  | 3x1701 |  | AI1700 |  | 0 | 2 |  |  | Actual status, Zone 8: 0 = Normal 1 = B-alarm 2 = A-alarm
| ZoneModule 8 - VAV Supply 1 Actuator Setpoint % | % | 3x1702 |  | AI1701 |  | 0 | 10000 |  |  | Zone 8; Actual setpoint; VAV inlet damper no. 1 [1/100 %]
| ZoneModule 8 - VAV Supply 1 Actual Flow | m3/h | 3x1703 |  | AI1702 |  | 0 | 65535 |  |  | Zone 8; Actual air quantity; VAV inlet damper no. 1 [m3/h]
| ZoneModule 8 - VAV Supply 2 Actuator Setpoint % | % | 3x1704 |  | AI1703 |  | 0 | 10000 |  |  | Zone 8; Actual setpoint; VAV inlet damper no. 2 [1/100 %]
| ZoneModule 8 - VAV Supply 2 Actual Flow | m3/h | 3x1705 |  | AI1704 |  | 0 | 65535 |  |  | Zone 8; Actual air quantity; VAV inlet damper no. 2 [m3/h]
| ZoneModule 8 - VAV Extract Actuator Setpoint % | % | 3x1706 |  | AI1705 |  | 0 | 10000 |  |  | Zone 8; Actual setpoint; VAV exhaust damper [1/100 %]
| ZoneModule 8 - VAV Extract Actual Flow | m3/h | 3x1707 |  | AI1706 |  | 0 | 65535 |  |  | Zone 8; Actual air quantity; VAV exhaust damper [m3/h]
| ZoneModule 8 - Heating Valve Setpoint % | % | 3x1708 |  | AI1707 |  | 0 | 10000 |  |  | Zone 8; Actual opening, heating valve [1/100 %]
| ZoneModule 8 - Cooling Valve Setpoint % | % | 3x1709 |  | AI1708 |  | 0 | 10000 |  |  | Zone 8; Actual opening, cooling valve [1/100 %]
| ZoneModule 8 - Room Temperature Actual Value | °C | 3x1710 |  | AI1709 |  | -4000 | 10000 |  |  | Zone 8; Actual room temperature [1/100 °C]
| ZoneModule 8 - Supply Temperature Actual Value | °C | 3x1711 |  | AI1710 |  | -4000 | 10000 |  |  | Zone 8; Actual inlet temperature [1/100 °C]
| ZoneModule 8 - Remote Setpoint Offset Actual Value | K | 3x1712 |  | AI1711 |  | -4000 | 10000 |  |  | Zone 8; Actual temperature offset from potentiometer [1/100 °C]
| ZoneModule 8 - CO2/VOC Actual Value | ppm | 3x1713 |  | AI1712 |  | 0 | 5000 |  |  | Zone 8; Actual CO2/VOC level [ppm]
| ZoneModule 8 - RH Actual Value | rh | 3x1714 |  | AI1713 |  | 0 | 10000 |  |  | Zone 8; Actual relative humidity level [%rh]
| ZoneModule 8 - Room Temperature Actual Setpoint | °C | 3x1715 |  | AI1714 |  | -4000 | 10000 |  |  | Zone 8; Actual controller setpoint, room temperature [1/100 °C]
| ZoneModule 8 - Room Panel Air Mode |  | 3x1716 | 3.30 | AI1715 | 3.30 | 0 | 3 |  |  | Zone 8; RPT-20 Room Panel; Actual Air Mode: 0 = Auto 1 = Low 2 = High 3 = Stop
| ZoneModule 8 - Heating Valve Actual Flow | l/h | 3x1717 | 3.30 | AI1716 | 3.30 | 0 | 65535 |  |  | Zone 8; Actual Flow; Heating Valve [l/h]
| ZoneModule 8 - Cooling Valve Actual Flow | l/h | 3x1718 | 3.30 | AI1717 | 3.30 | 0 | 65535 |  |  | Zone 8; Actual Flow; Cooling Valve [l/h]
| ZoneModule 8 - VAV Supply 1 Actual Damper pos. % | % | 3x1719 | 3.30 | AI1718 | 3.30 | 0 | 10000 |  |  | Zone 8; Actual setpoint; VAV Supply 1 damper no. 1 [1/100 %]
| ZoneModule 8 - VAV Supply 2 Actual Damper pos. % | % | 3x1720 | 3.30 | AI1719 | 3.30 | 0 | 10000 |  |  | Zone 8; Actual air quantity;VAV Supply 1 damper no. 1 [m3/h]
| ZoneModule 8 - VAV Extract Actual Damper pos. % | % | 3x1721 | 3.30 | AI1720 | 3.30 | 0 | 10000 |  |  | Zone 8; Actual position; VAV Extract 1 damper no. 1 [1/100 %]
| ZoneModule 8 - EL Heater 1 Temp. Sensor Value | °C | 3x1722 | 3.40 | AI1721 | 3.40 | -4000 | 10000 |  |  | Zone 8; Electric heating Coil 1; Sensor Temperature [1/100 °C]
| ZoneModule 8 - EL Heater 2 Temp. Sensor Value | °C | 3x1723 | 3.40 | AI1722 | 3.40 | -4000 | 10000 |  |  | Zone 8; Electric heating Coil 2; Sensor Temperature [1/100 °C]
| ZoneModule 8 - Ext Aout1 Output | % | 3x1724 | 3.40 | AI1723 | 3.40 | 0 | 10000 |  |  | Zone 8; Extension Module; Actual value Analog Output Aout1 [1/100 V]
| ZoneModule 8 - Ext Aout2 Output | % | 3x1725 | 3.40 | AI1724 | 3.40 | 0 | 10000 |  |  | Zone 8; Extension Module; Actual value Analog Output Aout2 [1/100 V]
| ZoneModule 8 - ZoneModule Alarm Bitmap 1 |  | 3x1726 | 3.40 | AI1725 | 3.40 | 0 | 65535 |  |  | Zone 8; Alarm Bit Map 1 - see tab below: Bit Map Alarm Overview
| ZoneModule 8 - ZoneModule Alarm Bitmap 2 |  | 3x1727 | 3.40 | AI1726 | 3.40 | 0 | 65535 |  |  | Zone 8; Alarm Bit Map 2 - see tab below: Bit Map Alarm Overview
| ZoneModule 8 - ZoneModule Alarm Bitmap 3 |  | 3x1728 | 3.40 | AI1727 | 3.40 | 0 | 65535 |  |  | Zone 8; Alarm Bit Map 3 - see tab below: Bit Map Alarm Overview
| ZoneModule 8 - ZoneModule Alarm Bitmap 4 |  | 3x1729 | 3.40 | AI1728 | 3.40 | 0 | 65535 |  |  | Zone 8; Alarm Bit Map 4 - see tab below: Bit Map Alarm Overview
| ZoneModule 8 - VAV Extract 2 Actuator Setpoint % | % | 3x1730 | 3.40 | AI1729 | 3.40 | 0 | 10000 |  |  | Zone 8; Actual setpoint; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 8 - VAV Extract 2 Actual Flow | m3/h | 3x1731 | 3.40 | AI1730 | 3.40 | 0 | 65535 |  |  | Zone 8; Actual air quantity;VAV Extract 2 damper no. 1 [m3/h]
| ZoneModule 8 - VAV Extract 2 Actual Damper pos. % | % | 3x1732 | 3.40 | AI1731 | 3.40 | 0 | 10000 |  |  | Zone 8; Actual position; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 9 - Status |  | 3x1801 |  | AI1800 |  | 0 | 2 |  |  | Actual status, Zone 9: 0 = Normal 1 = B-alarm 2 = A-alarm
| ZoneModule 9 - VAV Supply 1 Actuator Setpoint % | % | 3x1802 |  | AI1801 |  | 0 | 10000 |  |  | Zone 9; Actual setpoint; VAV inlet damper no. 1 [1/100 %]
| ZoneModule 9 - VAV Supply 1 Actual Flow | m3/h | 3x1803 |  | AI1802 |  | 0 | 65535 |  |  | Zone 9; Actual air quantity; VAV inlet damper no. 1 [m3/h]
| ZoneModule 9 - VAV Supply 2 Actuator Setpoint % | % | 3x1804 |  | AI1803 |  | 0 | 10000 |  |  | Zone 9; Actual setpoint; VAV inlet damper no. 2 [1/100 %]
| ZoneModule 9 - VAV Supply 2 Actual Flow | m3/h | 3x1805 |  | AI1804 |  | 0 | 65535 |  |  | Zone 9; Actual air quantity; VAV inlet damper no. 2 [m3/h]
| ZoneModule 9 - VAV Extract Actuator Setpoint % | % | 3x1806 |  | AI1805 |  | 0 | 10000 |  |  | Zone 9; Actual setpoint; VAV exhaust damper [1/100 %]
| ZoneModule 9 - VAV Extract Actual Flow | m3/h | 3x1807 |  | AI1806 |  | 0 | 65535 |  |  | Zone 9; Actual air quantity; VAV exhaust damper [m3/h]
| ZoneModule 9 - Heating Valve Setpoint % | % | 3x1808 |  | AI1807 |  | 0 | 10000 |  |  | Zone 9; Actual opening, heating valve [1/100 %]
| ZoneModule 9 - Cooling Valve Setpoint % | % | 3x1809 |  | AI1808 |  | 0 | 10000 |  |  | Zone 9; Actual opening, cooling valve [1/100 %]
| ZoneModule 9 - Room Temperature Actual Value | °C | 3x1810 |  | AI1809 |  | -4000 | 10000 |  |  | Zone 9; Actual room temperature [1/100 °C]
| ZoneModule 9 - Supply Temperature Actual Value | °C | 3x1811 |  | AI1810 |  | -4000 | 10000 |  |  | Zone 9; Actual inlet temperature [1/100 °C]
| ZoneModule 9 - Remote Setpoint Offset Actual Value | K | 3x1812 |  | AI1811 |  | -4000 | 10000 |  |  | Zone 9; Actual temperature offset from potentiometer [1/100 °C]
| ZoneModule 9 - CO2/VOC Actual Value | ppm | 3x1813 |  | AI1812 |  | 0 | 5000 |  |  | Zone 9; Actual CO2/VOC level [ppm]
| ZoneModule 9 - RH Actual Value | rh | 3x1814 |  | AI1813 |  | 0 | 10000 |  |  | Zone 9; Actual relative humidity level [%rh]
| ZoneModule 9 - Room Temperature Actual Setpoint | °C | 3x1815 |  | AI1814 |  | -4000 | 10000 |  |  | Zone 9; Actual controller setpoint, room temperature [1/100 °C]
| ZoneModule 9 - Room Panel Air Mode |  | 3x1816 | 3.30 | AI1815 | 3.30 | 0 | 3 |  |  | Zone 9; RPT-20 Room Panel; Actual Air Mode: 0 = Auto 1 = Low 2 = High 3 = Stop
| ZoneModule 9 - Heating Valve Actual Flow | l/h | 3x1817 | 3.30 | AI1816 | 3.30 | 0 | 65535 |  |  | Zone 9; Actual Flow; Heating Valve [l/h]
| ZoneModule 9 - Cooling Valve Actual Flow | l/h | 3x1818 | 3.30 | AI1817 | 3.30 | 0 | 65535 |  |  | Zone 9; Actual Flow; Cooling Valve [l/h]
| ZoneModule 9 - VAV Supply 1 Actual Damper pos. % | % | 3x1819 | 3.30 | AI1818 | 3.30 | 0 | 10000 |  |  | Zone 9; Actual setpoint; VAV Supply 1 damper no. 1 [1/100 %]
| ZoneModule 9 - VAV Supply 2 Actual Damper pos. % | % | 3x1820 | 3.30 | AI1819 | 3.30 | 0 | 10000 |  |  | Zone 9; Actual air quantity;VAV Supply 1 damper no. 1 [m3/h]
| ZoneModule 9 - VAV Extract Actual Damper pos. % | % | 3x1821 | 3.30 | AI1820 | 3.30 | 0 | 10000 |  |  | Zone 9; Actual position; VAV Extract 1 damper no. 1 [1/100 %]
| ZoneModule 9 - EL Heater 1 Temp. Sensor Value | °C | 3x1822 | 3.40 | AI1821 | 3.40 | -4000 | 10000 |  |  | Zone 9; Electric heating Coil 1; Sensor Temperature [1/100 °C]
| ZoneModule 9 - EL Heater 2 Temp. Sensor Value | °C | 3x1823 | 3.40 | AI1822 | 3.40 | -4000 | 10000 |  |  | Zone 9; Electric heating Coil 2; Sensor Temperature [1/100 °C]
| ZoneModule 9 - Ext Aout1 Output | % | 3x1824 | 3.40 | AI1823 | 3.40 | 0 | 10000 |  |  | Zone 9; Extension Module; Actual value Analog Output Aout1 [1/100 V]
| ZoneModule 9 - Ext Aout2 Output | % | 3x1825 | 3.40 | AI1824 | 3.40 | 0 | 10000 |  |  | Zone 9; Extension Module; Actual value Analog Output Aout2 [1/100 V]
| ZoneModule 9 - ZoneModule Alarm Bitmap 1 |  | 3x1826 | 3.40 | AI1825 | 3.40 | 0 | 65535 |  |  | Zone 9; Alarm Bit Map 1 - see tab below: Bit Map Alarm Overview
| ZoneModule 9 - ZoneModule Alarm Bitmap 2 |  | 3x1827 | 3.40 | AI1826 | 3.40 | 0 | 65535 |  |  | Zone 9; Alarm Bit Map 2 - see tab below: Bit Map Alarm Overview
| ZoneModule 9 - ZoneModule Alarm Bitmap 3 |  | 3x1828 | 3.40 | AI1827 | 3.40 | 0 | 65535 |  |  | Zone 9; Alarm Bit Map 3 - see tab below: Bit Map Alarm Overview
| ZoneModule 9 - ZoneModule Alarm Bitmap 4 |  | 3x1829 | 3.40 | AI1828 | 3.40 | 0 | 65535 |  |  | Zone 9; Alarm Bit Map 4 - see tab below: Bit Map Alarm Overview
| ZoneModule 9 - VAV Extract 2 Actuator Setpoint % | % | 3x1830 | 3.40 | AI1829 | 3.40 | 0 | 10000 |  |  | Zone 9; Actual setpoint; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 9 - VAV Extract 2 Actual Flow | m3/h | 3x1831 | 3.40 | AI1830 | 3.40 | 0 | 65535 |  |  | Zone 9; Actual air quantity;VAV Extract 2 damper no. 1 [m3/h]
| ZoneModule 9 - VAV Extract 2 Actual Damper pos. % | % | 3x1832 | 3.40 | AI1831 | 3.40 | 0 | 10000 |  |  | Zone 9; Actual position; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 10 - Status |  | 3x1901 |  | AI1900 |  | 0 | 2 |  |  | Actual status, Zone 10: 0 = Normal 1 = B-alarm 2 = A-alarm
| ZoneModule 10 - VAV Supply 1 Actuator Setpoint % | % | 3x1902 |  | AI1901 |  | 0 | 10000 |  |  | Zone 10; Actual setpoint; VAV inlet damper no. 1 [1/100 %]
| ZoneModule 10 - VAV Supply 1 Actual Flow | m3/h | 3x1903 |  | AI1902 |  | 0 | 65535 |  |  | Zone 10; Actual air quantity; VAV inlet damper no. 1 [m3/h]
| ZoneModule 10 - VAV Supply 2 Actuator Setpoint % | % | 3x1904 |  | AI1903 |  | 0 | 10000 |  |  | Zone 10; Actual setpoint; VAV inlet damper no. 2 [1/100 %]
| ZoneModule 10 - VAV Supply 2 Actual Flow | m3/h | 3x1905 |  | AI1904 |  | 0 | 65535 |  |  | Zone 10; Actual air quantity; VAV inlet damper no. 2 [m3/h]
| ZoneModule 10 - VAV Extract Actuator Setpoint % | % | 3x1906 |  | AI1905 |  | 0 | 10000 |  |  | Zone 10; Actual setpoint; VAV exhaust damper [1/100 %]
| ZoneModule 10 - VAV Extract Actual Flow | m3/h | 3x1907 |  | AI1906 |  | 0 | 65535 |  |  | Zone 10; Actual air quantity; VAV exhaust damper [m3/h]
| ZoneModule 10 - Heating Valve Setpoint % | % | 3x1908 |  | AI1907 |  | 0 | 10000 |  |  | Zone 10; Actual opening, heating valve [1/100 %]
| ZoneModule 10 - Cooling Valve Setpoint % | % | 3x1909 |  | AI1908 |  | 0 | 10000 |  |  | Zone 10; Actual opening, cooling valve [1/100 %]
| ZoneModule 10 - Room Temperature Actual Value | °C | 3x1910 |  | AI1909 |  | -4000 | 10000 |  |  | Zone 10; Actual room temperature [1/100 °C]
| ZoneModule 10 - Supply Temperature Actual Value | °C | 3x1911 |  | AI1910 |  | -4000 | 10000 |  |  | Zone 10; Actual inlet temperature [1/100 °C]
| ZoneModule 10 - Remote Setpoint Offset Actual Value | K | 3x1912 |  | AI1911 |  | -4000 | 10000 |  |  | Zone 10; Actual temperature offset from potentiometer [1/100 °C]
| ZoneModule 10 - CO2/VOC Actual Value | ppm | 3x1913 |  | AI1912 |  | 0 | 5000 |  |  | Zone 10; Actual CO2/VOC level [ppm]
| ZoneModule 10 - RH Actual Value | rh | 3x1914 |  | AI1913 |  | 0 | 10000 |  |  | Zone 10; Actual relative humidity level [%rh]
| ZoneModule 10 - Room Temperature Actual Setpoint | °C | 3x1915 |  | AI1914 |  | -4000 | 10000 |  |  | Zone 10; Actual controller setpoint, room temperature [1/100 °C]
| ZoneModule 10 - Room Panel Air Mode |  | 3x1916 | 3.30 | AI1915 | 3.30 | 0 | 3 |  |  | Zone 10; RPT-20 Room Panel; Actual Air Mode: 0 = Auto 1 = Low 2 = High 3 = Stop
| ZoneModule 10 - Heating Valve Actual Flow | l/h | 3x1917 | 3.30 | AI1916 | 3.30 | 0 | 65535 |  |  | Zone 10; Actual Flow; Heating Valve [l/h]
| ZoneModule 10 - Cooling Valve Actual Flow | l/h | 3x1918 | 3.30 | AI1917 | 3.30 | 0 | 65535 |  |  | Zone 10; Actual Flow; Cooling Valve [l/h]
| ZoneModule 10 - VAV Supply 1 Actual Damper pos. % | % | 3x1919 | 3.30 | AI1918 | 3.30 | 0 | 10000 |  |  | Zone 10; Actual setpoint; VAV Supply 1 damper no. 1 [1/100 %]
| ZoneModule 10 - VAV Supply 2 Actual Damper pos. % | % | 3x1920 | 3.30 | AI1919 | 3.30 | 0 | 10000 |  |  | Zone 10; Actual air quantity;VAV Supply 1 damper no. 1 [m3/h]
| ZoneModule 10 - VAV Extract Actual Damper pos. % | % | 3x1921 | 3.30 | AI1920 | 3.30 | 0 | 10000 |  |  | Zone 10; Actual position; VAV Extract 1 damper no. 1 [1/100 %]
| ZoneModule 10 - EL Heater 1 Temp. Sensor Value | °C | 3x1922 | 3.40 | AI1921 | 3.40 | -4000 | 10000 |  |  | Zone 10; Electric heating Coil 1; Sensor Temperature [1/100 °C]
| ZoneModule 10 - EL Heater 2 Temp. Sensor Value | °C | 3x1923 | 3.40 | AI1922 | 3.40 | -4000 | 10000 |  |  | Zone 10; Electric heating Coil 2; Sensor Temperature [1/100 °C]
| ZoneModule 10 - Ext Aout1 Output | % | 3x1924 | 3.40 | AI1923 | 3.40 | 0 | 10000 |  |  | Zone 10; Extension Module; Actual value Analog Output Aout1 [1/100 V]
| ZoneModule 10 - Ext Aout2 Output | % | 3x1925 | 3.40 | AI1924 | 3.40 | 0 | 10000 |  |  | Zone 10; Extension Module; Actual value Analog Output Aout2 [1/100 V]
| ZoneModule 10 - ZoneModule Alarm Bitmap 1 |  | 3x1926 | 3.40 | AI1925 | 3.40 | 0 | 65535 |  |  | Zone 10; Alarm Bit Map 1 - see tab below: Bit Map Alarm Overview
| ZoneModule 10 - ZoneModule Alarm Bitmap 2 |  | 3x1927 | 3.40 | AI1926 | 3.40 | 0 | 65535 |  |  | Zone 10; Alarm Bit Map 2 - see tab below: Bit Map Alarm Overview
| ZoneModule 10 - ZoneModule Alarm Bitmap 3 |  | 3x1928 | 3.40 | AI1927 | 3.40 | 0 | 65535 |  |  | Zone 10; Alarm Bit Map 3 - see tab below: Bit Map Alarm Overview
| ZoneModule 10 - ZoneModule Alarm Bitmap 4 |  | 3x1929 | 3.40 | AI1928 | 3.40 | 0 | 65535 |  |  | Zone 10; Alarm Bit Map 4 - see tab below: Bit Map Alarm Overview
| ZoneModule 10 - VAV Extract 2 Actuator Setpoint % | % | 3x1930 | 3.40 | AI1929 | 3.40 | 0 | 10000 |  |  | Zone 10; Actual setpoint; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 10 - VAV Extract 2 Actual Flow | m3/h | 3x1931 | 3.40 | AI1930 | 3.40 | 0 | 65535 |  |  | Zone 10; Actual air quantity;VAV Extract 2 damper no. 1 [m3/h]
| ZoneModule 10 - VAV Extract 2 Actual Damper pos. % | % | 3x1932 | 3.40 | AI1931 | 3.40 | 0 | 10000 |  |  | Zone 10; Actual position; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 11 - Status |  | 3x2001 |  | AI2000 |  | 0 | 2 |  |  | Actual status, Zone 11: 0 = Normal 1 = B-alarm 2 = A-alarm
| ZoneModule 11 - VAV Supply 1 Actuator Setpoint % | % | 3x2002 |  | AI2001 |  | 0 | 10000 |  |  | Zone 11; Actual setpoint; VAV inlet damper no. 1 [1/100 %]
| ZoneModule 11 - VAV Supply 1 Actual Flow | m3/h | 3x2003 |  | AI2002 |  | 0 | 65535 |  |  | Zone 11; Actual air quantity; VAV inlet damper no. 1 [m3/h]
| ZoneModule 11 - VAV Supply 2 Actuator Setpoint % | % | 3x2004 |  | AI2003 |  | 0 | 10000 |  |  | Zone 11; Actual setpoint; VAV inlet damper no. 2 [1/100 %]
| ZoneModule 11 - VAV Supply 2 Actual Flow | m3/h | 3x2005 |  | AI2004 |  | 0 | 65535 |  |  | Zone 11; Actual air quantity; VAV inlet damper no. 2 [m3/h]
| ZoneModule 11 - VAV Extract Actuator Setpoint % | % | 3x2006 |  | AI2005 |  | 0 | 10000 |  |  | Zone 11; Actual setpoint; VAV exhaust damper [1/100 %]
| ZoneModule 11 - VAV Extract Actual Flow | m3/h | 3x2007 |  | AI2006 |  | 0 | 65535 |  |  | Zone 11; Actual air quantity; VAV exhaust damper [m3/h]
| ZoneModule 11 - Heating Valve Setpoint % | % | 3x2008 |  | AI2007 |  | 0 | 10000 |  |  | Zone 11; Actual opening, heating valve [1/100 %]
| ZoneModule 11 - Cooling Valve Setpoint % | % | 3x2009 |  | AI2008 |  | 0 | 10000 |  |  | Zone 11; Actual opening, cooling valve [1/100 %]
| ZoneModule 11 - Room Temperature Actual Value | °C | 3x2010 |  | AI2009 |  | -4000 | 10000 |  |  | Zone 11; Actual room temperature [1/100 °C]
| ZoneModule 11 - Supply Temperature Actual Value | °C | 3x2011 |  | AI2010 |  | -4000 | 10000 |  |  | Zone 11; Actual inlet temperature [1/100 °C]
| ZoneModule 11 - Remote Setpoint Offset Actual Value | K | 3x2012 |  | AI2011 |  | -4000 | 10000 |  |  | Zone 11; Actual temperature offset from potentiometer [1/100 °C]
| ZoneModule 11 - CO2/VOC Actual Value | ppm | 3x2013 |  | AI2012 |  | 0 | 5000 |  |  | Zone 11; Actual CO2/VOC level [ppm]
| ZoneModule 11 - RH Actual Value | rh | 3x2014 |  | AI2013 |  | 0 | 10000 |  |  | Zone 11; Actual relative humidity level [%rh]
| ZoneModule 11 - Room Temperature Actual Setpoint | °C | 3x2015 |  | AI2014 |  | -4000 | 10000 |  |  | Zone 11; Actual controller setpoint, room temperature [1/100 °C]
| ZoneModule 11 - Room Panel Air Mode |  | 3x2016 | 3.30 | AI2015 | 3.30 | 0 | 3 |  |  | Zone 11; RPT-20 Room Panel; Actual Air Mode: 0 = Auto 1 = Low 2 = High 3 = Stop
| ZoneModule 11 - Heating Valve Actual Flow | l/h | 3x2017 | 3.30 | AI2016 | 3.30 | 0 | 65535 |  |  | Zone 11; Actual Flow; Heating Valve [l/h]
| ZoneModule 11 - Cooling Valve Actual Flow | l/h | 3x2018 | 3.30 | AI2017 | 3.30 | 0 | 65535 |  |  | Zone 11; Actual Flow; Cooling Valve [l/h]
| ZoneModule 11 - VAV Supply 1 Actual Damper pos. % | % | 3x2019 | 3.30 | AI2018 | 3.30 | 0 | 10000 |  |  | Zone 11; Actual setpoint; VAV Supply 1 damper no. 1 [1/100 %]
| ZoneModule 11 - VAV Supply 2 Actual Damper pos. % | % | 3x2020 | 3.30 | AI2019 | 3.30 | 0 | 10000 |  |  | Zone 11; Actual air quantity;VAV Supply 1 damper no. 1 [m3/h]
| ZoneModule 11 - VAV Extract Actual Damper pos. % | % | 3x2021 | 3.30 | AI2020 | 3.30 | 0 | 10000 |  |  | Zone 11; Actual position; VAV Extract 1 damper no. 1 [1/100 %]
| ZoneModule 11 - EL Heater 1 Temp. Sensor Value | °C | 3x2022 | 3.40 | AI2021 | 3.40 | -4000 | 10000 |  |  | Zone 11; Electric heating Coil 1; Sensor Temperature [1/100 °C]
| ZoneModule 11 - EL Heater 2 Temp. Sensor Value | °C | 3x2023 | 3.40 | AI2022 | 3.40 | -4000 | 10000 |  |  | Zone 11; Electric heating Coil 2; Sensor Temperature [1/100 °C]
| ZoneModule 11 - Ext Aout1 Output | % | 3x2024 | 3.40 | AI2023 | 3.40 | 0 | 10000 |  |  | Zone 11; Extension Module; Actual value Analog Output Aout1 [1/100 V]
| ZoneModule 11 - Ext Aout2 Output | % | 3x2025 | 3.40 | AI2024 | 3.40 | 0 | 10000 |  |  | Zone 11; Extension Module; Actual value Analog Output Aout2 [1/100 V]
| ZoneModule 11 - ZoneModule Alarm Bitmap 1 |  | 3x2026 | 3.40 | AI2025 | 3.40 | 0 | 65535 |  |  | Zone 11; Alarm Bit Map 1 - see tab below: Bit Map Alarm Overview
| ZoneModule 11 - ZoneModule Alarm Bitmap 2 |  | 3x2027 | 3.40 | AI2026 | 3.40 | 0 | 65535 |  |  | Zone 11; Alarm Bit Map 2 - see tab below: Bit Map Alarm Overview
| ZoneModule 11 - ZoneModule Alarm Bitmap 3 |  | 3x2028 | 3.40 | AI2027 | 3.40 | 0 | 65535 |  |  | Zone 11; Alarm Bit Map 3 - see tab below: Bit Map Alarm Overview
| ZoneModule 11 - ZoneModule Alarm Bitmap 4 |  | 3x2029 | 3.40 | AI2028 | 3.40 | 0 | 65535 |  |  | Zone 11; Alarm Bit Map 4 - see tab below: Bit Map Alarm Overview
| ZoneModule 11 - VAV Extract 2 Actuator Setpoint % | % | 3x2030 | 3.40 | AI2029 | 3.40 | 0 | 10000 |  |  | Zone 11; Actual setpoint; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 11 - VAV Extract 2 Actual Flow | m3/h | 3x2031 | 3.40 | AI2030 | 3.40 | 0 | 65535 |  |  | Zone 11; Actual air quantity;VAV Extract 2 damper no. 1 [m3/h]
| ZoneModule 11 - VAV Extract 2 Actual Damper pos. % | % | 3x2032 | 3.40 | AI2031 | 3.40 | 0 | 10000 |  |  | Zone 11; Actual position; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 12 - Status |  | 3x2101 |  | AI2100 |  | 0 | 2 |  |  | Actual status, Zone 12: 0 = Normal 1 = B-alarm 2 = A-alarm
| ZoneModule 12 - VAV Supply 1 Actuator Setpoint % | % | 3x2102 |  | AI2101 |  | 0 | 10000 |  |  | Zone 12; Actual setpoint; VAV inlet damper no. 1 [1/100 %]
| ZoneModule 12 - VAV Supply 1 Actual Flow | m3/h | 3x2103 |  | AI2102 |  | 0 | 65535 |  |  | Zone 12; Actual air quantity; VAV inlet damper no. 1 [m3/h]
| ZoneModule 12 - VAV Supply 2 Actuator Setpoint % | % | 3x2104 |  | AI2103 |  | 0 | 10000 |  |  | Zone 12; Actual setpoint; VAV inlet damper no. 2 [1/100 %]
| ZoneModule 12 - VAV Supply 2 Actual Flow | m3/h | 3x2105 |  | AI2104 |  | 0 | 65535 |  |  | Zone 12; Actual air quantity; VAV inlet damper no. 2 [m3/h]
| ZoneModule 12 - VAV Extract Actuator Setpoint % | % | 3x2106 |  | AI2105 |  | 0 | 10000 |  |  | Zone 12; Actual setpoint; VAV exhaust damper [1/100 %]
| ZoneModule 12 - VAV Extract Actual Flow | m3/h | 3x2107 |  | AI2106 |  | 0 | 65535 |  |  | Zone 12; Actual air quantity; VAV exhaust damper [m3/h]
| ZoneModule 12 - Heating Valve Setpoint % | % | 3x2108 |  | AI2107 |  | 0 | 10000 |  |  | Zone 12; Actual opening, heating valve [1/100 %]
| ZoneModule 12 - Cooling Valve Setpoint % | % | 3x2109 |  | AI2108 |  | 0 | 10000 |  |  | Zone 12; Actual opening, cooling valve [1/100 %]
| ZoneModule 12 - Room Temperature Actual Value | °C | 3x2110 |  | AI2109 |  | -4000 | 10000 |  |  | Zone 12; Actual room temperature [1/100 °C]
| ZoneModule 12 - Supply Temperature Actual Value | °C | 3x2111 |  | AI2110 |  | -4000 | 10000 |  |  | Zone 12; Actual inlet temperature [1/100 °C]
| ZoneModule 12 - Remote Setpoint Offset Actual Value | K | 3x2112 |  | AI2111 |  | -4000 | 10000 |  |  | Zone 12; Actual temperature offset from potentiometer [1/100 °C]
| ZoneModule 12 - CO2/VOC Actual Value | ppm | 3x2113 |  | AI2112 |  | 0 | 5000 |  |  | Zone 12; Actual CO2/VOC level [ppm]
| ZoneModule 12 - RH Actual Value | rh | 3x2114 |  | AI2113 |  | 0 | 10000 |  |  | Zone 12; Actual relative humidity level [%rh]
| ZoneModule 12 - Room Temperature Actual Setpoint | °C | 3x2115 |  | AI2114 |  | -4000 | 10000 |  |  | Zone 12; Actual controller setpoint, room temperature [1/100 °C]
| ZoneModule 12 - Room Panel Air Mode |  | 3x2116 | 3.30 | AI2115 | 3.30 | 0 | 3 |  |  | Zone 12; RPT-20 Room Panel; Actual Air Mode: 0 = Auto 1 = Low 2 = High 3 = Stop
| ZoneModule 12 - Heating Valve Actual Flow | l/h | 3x2117 | 3.30 | AI2116 | 3.30 | 0 | 65535 |  |  | Zone 12; Actual Flow; Heating Valve [l/h]
| ZoneModule 12 - Cooling Valve Actual Flow | l/h | 3x2118 | 3.30 | AI2117 | 3.30 | 0 | 65535 |  |  | Zone 12; Actual Flow; Cooling Valve [l/h]
| ZoneModule 12 - VAV Supply 1 Actual Damper pos. % | % | 3x2119 | 3.30 | AI2118 | 3.30 | 0 | 10000 |  |  | Zone 12; Actual setpoint; VAV Supply 1 damper no. 1 [1/100 %]
| ZoneModule 12 - VAV Supply 2 Actual Damper pos. % | % | 3x2120 | 3.30 | AI2119 | 3.30 | 0 | 10000 |  |  | Zone 12; Actual air quantity;VAV Supply 1 damper no. 1 [m3/h]
| ZoneModule 12 - VAV Extract Actual Damper pos. % | % | 3x2121 | 3.30 | AI2120 | 3.30 | 0 | 10000 |  |  | Zone 12; Actual position; VAV Extract 1 damper no. 1 [1/100 %]
| ZoneModule 12 - EL Heater 1 Temp. Sensor Value | °C | 3x2122 | 3.40 | AI2121 | 3.40 | -4000 | 10000 |  |  | Zone 12; Electric heating Coil 1; Sensor Temperature [1/100 °C]
| ZoneModule 12 - EL Heater 2 Temp. Sensor Value | °C | 3x2123 | 3.40 | AI2122 | 3.40 | -4000 | 10000 |  |  | Zone 12; Electric heating Coil 2; Sensor Temperature [1/100 °C]
| ZoneModule 12 - Ext Aout1 Output | % | 3x2124 | 3.40 | AI2123 | 3.40 | 0 | 10000 |  |  | Zone 12; Extension Module; Actual value Analog Output Aout1 [1/100 V]
| ZoneModule 12 - Ext Aout2 Output | % | 3x2125 | 3.40 | AI2124 | 3.40 | 0 | 10000 |  |  | Zone 12; Extension Module; Actual value Analog Output Aout2 [1/100 V]
| ZoneModule 12 - ZoneModule Alarm Bitmap 1 |  | 3x2126 | 3.40 | AI2125 | 3.40 | 0 | 65535 |  |  | Zone 12; Alarm Bit Map 1 - see tab below: Bit Map Alarm Overview
| ZoneModule 12 - ZoneModule Alarm Bitmap 2 |  | 3x2127 | 3.40 | AI2126 | 3.40 | 0 | 65535 |  |  | Zone 12; Alarm Bit Map 2 - see tab below: Bit Map Alarm Overview
| ZoneModule 12 - ZoneModule Alarm Bitmap 3 |  | 3x2128 | 3.40 | AI2127 | 3.40 | 0 | 65535 |  |  | Zone 12; Alarm Bit Map 3 - see tab below: Bit Map Alarm Overview
| ZoneModule 12 - ZoneModule Alarm Bitmap 4 |  | 3x2129 | 3.40 | AI2128 | 3.40 | 0 | 65535 |  |  | Zone 12; Alarm Bit Map 4 - see tab below: Bit Map Alarm Overview
| ZoneModule 12 - VAV Extract 2 Actuator Setpoint % | % | 3x2130 | 3.40 | AI2129 | 3.40 | 0 | 10000 |  |  | Zone 12; Actual setpoint; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 12 - VAV Extract 2 Actual Flow | m3/h | 3x2131 | 3.40 | AI2130 | 3.40 | 0 | 65535 |  |  | Zone 12; Actual air quantity;VAV Extract 2 damper no. 1 [m3/h]
| ZoneModule 12 - VAV Extract 2 Actual Damper pos. % | % | 3x2132 | 3.40 | AI2131 | 3.40 | 0 | 10000 |  |  | Zone 12; Actual position; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 13 - Status |  | 3x2201 |  | AI2200 |  | 0 | 2 |  |  | Actual status, Zone 13: 0 = Normal 1 = B-alarm 2 = A-alarm
| ZoneModule 13 - VAV Supply 1 Actuator Setpoint % | % | 3x2202 |  | AI2201 |  | 0 | 10000 |  |  | Zone 13; Actual setpoint; VAV inlet damper no. 1 [1/100 %]
| ZoneModule 13 - VAV Supply 1 Actual Flow | m3/h | 3x2203 |  | AI2202 |  | 0 | 65535 |  |  | Zone 13; Actual air quantity; VAV inlet damper no. 1 [m3/h]
| ZoneModule 13 - VAV Supply 2 Actuator Setpoint % | % | 3x2204 |  | AI2203 |  | 0 | 10000 |  |  | Zone 13; Actual setpoint; VAV inlet damper no. 2 [1/100 %]
| ZoneModule 13 - VAV Supply 2 Actual Flow | m3/h | 3x2205 |  | AI2204 |  | 0 | 65535 |  |  | Zone 13; Actual air quantity; VAV inlet damper no. 2 [m3/h]
| ZoneModule 13 - VAV Extract Actuator Setpoint % | % | 3x2206 |  | AI2205 |  | 0 | 10000 |  |  | Zone 13; Actual setpoint; VAV exhaust damper [1/100 %]
| ZoneModule 13 - VAV Extract Actual Flow | m3/h | 3x2207 |  | AI2206 |  | 0 | 65535 |  |  | Zone 13; Actual air quantity; VAV exhaust damper [m3/h]
| ZoneModule 13 - Heating Valve Setpoint % | % | 3x2208 |  | AI2207 |  | 0 | 10000 |  |  | Zone 13; Actual opening, heating valve [1/100 %]
| ZoneModule 13 - Cooling Valve Setpoint % | % | 3x2209 |  | AI2208 |  | 0 | 10000 |  |  | Zone 13; Actual opening, cooling valve [1/100 %]
| ZoneModule 13 - Room Temperature Actual Value | °C | 3x2210 |  | AI2209 |  | -4000 | 10000 |  |  | Zone 13; Actual room temperature [1/100 °C]
| ZoneModule 13 - Supply Temperature Actual Value | °C | 3x2211 |  | AI2210 |  | -4000 | 10000 |  |  | Zone 13; Actual inlet temperature [1/100 °C]
| ZoneModule 13 - Remote Setpoint Offset Actual Value | K | 3x2212 |  | AI2211 |  | -4000 | 10000 |  |  | Zone 13; Actual temperature offset from potentiometer [1/100 °C]
| ZoneModule 13 - CO2/VOC Actual Value | ppm | 3x2213 |  | AI2212 |  | 0 | 5000 |  |  | Zone 13; Actual CO2/VOC level [ppm]
| ZoneModule 13 - RH Actual Value | rh | 3x2214 |  | AI2213 |  | 0 | 10000 |  |  | Zone 13; Actual relative humidity level [%rh]
| ZoneModule 13 - Room Temperature Actual Setpoint | °C | 3x2215 |  | AI2214 |  | -4000 | 10000 |  |  | Zone 13; Actual controller setpoint, room temperature [1/100 °C]
| ZoneModule 13 - Room Panel Air Mode |  | 3x2216 | 3.30 | AI2215 | 3.30 | 0 | 3 |  |  | Zone 13; RPT-20 Room Panel; Actual Air Mode: 0 = Auto 1 = Low 2 = High 3 = Stop
| ZoneModule 13 - Heating Valve Actual Flow | l/h | 3x2217 | 3.30 | AI2216 | 3.30 | 0 | 65535 |  |  | Zone 13; Actual Flow; Heating Valve [l/h]
| ZoneModule 13 - Cooling Valve Actual Flow | l/h | 3x2218 | 3.30 | AI2217 | 3.30 | 0 | 65535 |  |  | Zone 13; Actual Flow; Cooling Valve [l/h]
| ZoneModule 13 - VAV Supply 1 Actual Damper pos. % | % | 3x2219 | 3.30 | AI2218 | 3.30 | 0 | 10000 |  |  | Zone 13; Actual setpoint; VAV Supply 1 damper no. 1 [1/100 %]
| ZoneModule 13 - VAV Supply 2 Actual Damper pos. % | % | 3x2220 | 3.30 | AI2219 | 3.30 | 0 | 10000 |  |  | Zone 13; Actual air quantity;VAV Supply 1 damper no. 1 [m3/h]
| ZoneModule 13 - VAV Extract Actual Damper pos. % | % | 3x2221 | 3.30 | AI2220 | 3.30 | 0 | 10000 |  |  | Zone 13; Actual position; VAV Extract 1 damper no. 1 [1/100 %]
| ZoneModule 13 - EL Heater 1 Temp. Sensor Value | °C | 3x2222 | 3.40 | AI2221 | 3.40 | -4000 | 10000 |  |  | Zone 13; Electric heating Coil 1; Sensor Temperature [1/100 °C]
| ZoneModule 13 - EL Heater 2 Temp. Sensor Value | °C | 3x2223 | 3.40 | AI2222 | 3.40 | -4000 | 10000 |  |  | Zone 13; Electric heating Coil 2; Sensor Temperature [1/100 °C]
| ZoneModule 13 - Ext Aout1 Output | % | 3x2224 | 3.40 | AI2223 | 3.40 | 0 | 10000 |  |  | Zone 13; Extension Module; Actual value Analog Output Aout1 [1/100 V]
| ZoneModule 13 - Ext Aout2 Output | % | 3x2225 | 3.40 | AI2224 | 3.40 | 0 | 10000 |  |  | Zone 13; Extension Module; Actual value Analog Output Aout2 [1/100 V]
| ZoneModule 13 - ZoneModule Alarm Bitmap 1 |  | 3x2226 | 3.40 | AI2225 | 3.40 | 0 | 65535 |  |  | Zone 13; Alarm Bit Map 1 - see tab below: Bit Map Alarm Overview
| ZoneModule 13 - ZoneModule Alarm Bitmap 2 |  | 3x2227 | 3.40 | AI2226 | 3.40 | 0 | 65535 |  |  | Zone 13; Alarm Bit Map 2 - see tab below: Bit Map Alarm Overview
| ZoneModule 13 - ZoneModule Alarm Bitmap 3 |  | 3x2228 | 3.40 | AI2227 | 3.40 | 0 | 65535 |  |  | Zone 13; Alarm Bit Map 3 - see tab below: Bit Map Alarm Overview
| ZoneModule 13 - ZoneModule Alarm Bitmap 4 |  | 3x2229 | 3.40 | AI2228 | 3.40 | 0 | 65535 |  |  | Zone 13; Alarm Bit Map 4 - see tab below: Bit Map Alarm Overview
| ZoneModule 13 - VAV Extract 2 Actuator Setpoint % | % | 3x2230 | 3.40 | AI2229 | 3.40 | 0 | 10000 |  |  | Zone 13; Actual setpoint; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 13 - VAV Extract 2 Actual Flow | m3/h | 3x2231 | 3.40 | AI2230 | 3.40 | 0 | 65535 |  |  | Zone 13; Actual air quantity;VAV Extract 2 damper no. 1 [m3/h]
| ZoneModule 13 - VAV Extract 2 Actual Damper pos. % | % | 3x2232 | 3.40 | AI2231 | 3.40 | 0 | 10000 |  |  | Zone 13; Actual position; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 14 - Status |  | 3x2301 |  | AI2300 |  | 0 | 2 |  |  | Actual status, Zone 14: 0 = Normal 1 = B-alarm 2 = A-alarm
| ZoneModule 14 - VAV Supply 1 Actuator Setpoint % | % | 3x2302 |  | AI2301 |  | 0 | 10000 |  |  | Zone 14; Actual setpoint; VAV inlet damper no. 1 [1/100 %]
| ZoneModule 14 - VAV Supply 1 Actual Flow | m3/h | 3x2303 |  | AI2302 |  | 0 | 65535 |  |  | Zone 14; Actual air quantity; VAV inlet damper no. 1 [m3/h]
| ZoneModule 14 - VAV Supply 2 Actuator Setpoint % | % | 3x2304 |  | AI2303 |  | 0 | 10000 |  |  | Zone 14; Actual setpoint; VAV inlet damper no. 2 [1/100 %]
| ZoneModule 14 - VAV Supply 2 Actual Flow | m3/h | 3x2305 |  | AI2304 |  | 0 | 65535 |  |  | Zone 14; Actual air quantity; VAV inlet damper no. 2 [m3/h]
| ZoneModule 14 - VAV Extract Actuator Setpoint % | % | 3x2306 |  | AI2305 |  | 0 | 10000 |  |  | Zone 14; Actual setpoint; VAV exhaust damper [1/100 %]
| ZoneModule 14 - VAV Extract Actual Flow | m3/h | 3x2307 |  | AI2306 |  | 0 | 65535 |  |  | Zone 14; Actual air quantity; VAV exhaust damper [m3/h]
| ZoneModule 14 - Heating Valve Setpoint % | % | 3x2308 |  | AI2307 |  | 0 | 10000 |  |  | Zone 14; Actual opening, heating valve [1/100 %]
| ZoneModule 14 - Cooling Valve Setpoint % | % | 3x2309 |  | AI2308 |  | 0 | 10000 |  |  | Zone 14; Actual opening, cooling valve [1/100 %]
| ZoneModule 14 - Room Temperature Actual Value | °C | 3x2310 |  | AI2309 |  | -4000 | 10000 |  |  | Zone 14; Actual room temperature [1/100 °C]
| ZoneModule 14 - Supply Temperature Actual Value | °C | 3x2311 |  | AI2310 |  | -4000 | 10000 |  |  | Zone 14; Actual inlet temperature [1/100 °C]
| ZoneModule 14 - Remote Setpoint Offset Actual Value | K | 3x2312 |  | AI2311 |  | -4000 | 10000 |  |  | Zone 14; Actual temperature offset from potentiometer [1/100 °C]
| ZoneModule 14 - CO2/VOC Actual Value | ppm | 3x2313 |  | AI2312 |  | 0 | 5000 |  |  | Zone 14; Actual CO2/VOC level [ppm]
| ZoneModule 14 - RH Actual Value | rh | 3x2314 |  | AI2313 |  | 0 | 10000 |  |  | Zone 14; Actual relative humidity level [%rh]
| ZoneModule 14 - Room Temperature Actual Setpoint | °C | 3x2315 |  | AI2314 |  | -4000 | 10000 |  |  | Zone 14; Actual controller setpoint, room temperature [1/100 °C]
| ZoneModule 14 - Room Panel Air Mode |  | 3x2316 | 3.30 | AI2315 | 3.30 | 0 | 3 |  |  | Zone 14; RPT-20 Room Panel; Actual Air Mode: 0 = Auto 1 = Low 2 = High 3 = Stop
| ZoneModule 14 - Heating Valve Actual Flow | l/h | 3x2317 | 3.30 | AI2316 | 3.30 | 0 | 65535 |  |  | Zone 14; Actual Flow; Heating Valve [l/h]
| ZoneModule 14 - Cooling Valve Actual Flow | l/h | 3x2318 | 3.30 | AI2317 | 3.30 | 0 | 65535 |  |  | Zone 14; Actual Flow; Cooling Valve [l/h]
| ZoneModule 14 - VAV Supply 1 Actual Damper pos. % | % | 3x2319 | 3.30 | AI2318 | 3.30 | 0 | 10000 |  |  | Zone 14; Actual setpoint; VAV Supply 1 damper no. 1 [1/100 %]
| ZoneModule 14 - VAV Supply 2 Actual Damper pos. % | % | 3x2320 | 3.30 | AI2319 | 3.30 | 0 | 10000 |  |  | Zone 14; Actual air quantity;VAV Supply 1 damper no. 1 [m3/h]
| ZoneModule 14 - VAV Extract Actual Damper pos. % | % | 3x2321 | 3.30 | AI2320 | 3.30 | 0 | 10000 |  |  | Zone 14; Actual position; VAV Extract 1 damper no. 1 [1/100 %]
| ZoneModule 14 - EL Heater 1 Temp. Sensor Value | °C | 3x2322 | 3.40 | AI2321 | 3.40 | -4000 | 10000 |  |  | Zone 14; Electric heating Coil 1; Sensor Temperature [1/100 °C]
| ZoneModule 14 - EL Heater 2 Temp. Sensor Value | °C | 3x2323 | 3.40 | AI2322 | 3.40 | -4000 | 10000 |  |  | Zone 14; Electric heating Coil 2; Sensor Temperature [1/100 °C]
| ZoneModule 14 - Ext Aout1 Output | % | 3x2324 | 3.40 | AI2323 | 3.40 | 0 | 10000 |  |  | Zone 14; Extension Module; Actual value Analog Output Aout1 [1/100 V]
| ZoneModule 14 - Ext Aout2 Output | % | 3x2325 | 3.40 | AI2324 | 3.40 | 0 | 10000 |  |  | Zone 14; Extension Module; Actual value Analog Output Aout2 [1/100 V]
| ZoneModule 14 - ZoneModule Alarm Bitmap 1 |  | 3x2326 | 3.40 | AI2325 | 3.40 | 0 | 65535 |  |  | Zone 14; Alarm Bit Map 1 - see tab below: Bit Map Alarm Overview
| ZoneModule 14 - ZoneModule Alarm Bitmap 2 |  | 3x2327 | 3.40 | AI2326 | 3.40 | 0 | 65535 |  |  | Zone 14; Alarm Bit Map 2 - see tab below: Bit Map Alarm Overview
| ZoneModule 14 - ZoneModule Alarm Bitmap 3 |  | 3x2328 | 3.40 | AI2327 | 3.40 | 0 | 65535 |  |  | Zone 14; Alarm Bit Map 3 - see tab below: Bit Map Alarm Overview
| ZoneModule 14 - ZoneModule Alarm Bitmap 4 |  | 3x2329 | 3.40 | AI2328 | 3.40 | 0 | 65535 |  |  | Zone 14; Alarm Bit Map 4 - see tab below: Bit Map Alarm Overview
| ZoneModule 14 - VAV Extract 2 Actuator Setpoint % | % | 3x2330 | 3.40 | AI2329 | 3.40 | 0 | 10000 |  |  | Zone 14; Actual setpoint; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 14 - VAV Extract 2 Actual Flow | m3/h | 3x2331 | 3.40 | AI2330 | 3.40 | 0 | 65535 |  |  | Zone 14; Actual air quantity;VAV Extract 2 damper no. 1 [m3/h]
| ZoneModule 14 - VAV Extract 2 Actual Damper pos. % | % | 3x2332 | 3.40 | AI2331 | 3.40 | 0 | 10000 |  |  | Zone 14; Actual position; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 15 - Status |  | 3x2401 |  | AI2400 |  | 0 | 2 |  |  | Actual status, Zone 15: 0 = Normal 1 = B-alarm 2 = A-alarm
| ZoneModule 15 - VAV Supply 1 Actuator Setpoint % | % | 3x2402 |  | AI2401 |  | 0 | 10000 |  |  | Zone 15; Actual setpoint; VAV inlet damper no. 1 [1/100 %]
| ZoneModule 15 - VAV Supply 1 Actual Flow | m3/h | 3x2403 |  | AI2402 |  | 0 | 65535 |  |  | Zone 15; Actual air quantity; VAV inlet damper no. 1 [m3/h]
| ZoneModule 15 - VAV Supply 2 Actuator Setpoint % | % | 3x2404 |  | AI2403 |  | 0 | 10000 |  |  | Zone 15; Actual setpoint; VAV inlet damper no. 2 [1/100 %]
| ZoneModule 15 - VAV Supply 2 Actual Flow | m3/h | 3x2405 |  | AI2404 |  | 0 | 65535 |  |  | Zone 15; Actual air quantity; VAV inlet damper no. 2 [m3/h]
| ZoneModule 15 - VAV Extract Actuator Setpoint % | % | 3x2406 |  | AI2405 |  | 0 | 10000 |  |  | Zone 15; Actual setpoint; VAV exhaust damper [1/100 %]
| ZoneModule 15 - VAV Extract Actual Flow | m3/h | 3x2407 |  | AI2406 |  | 0 | 65535 |  |  | Zone 15; Actual air quantity; VAV exhaust damper [m3/h]
| ZoneModule 15 - Heating Valve Setpoint % | % | 3x2408 |  | AI2407 |  | 0 | 10000 |  |  | Zone 15; Actual opening, heating valve [1/100 %]
| ZoneModule 15 - Cooling Valve Setpoint % | % | 3x2409 |  | AI2408 |  | 0 | 10000 |  |  | Zone 15; Actual opening, cooling valve [1/100 %]
| ZoneModule 15 - Room Temperature Actual Value | °C | 3x2410 |  | AI2409 |  | -4000 | 10000 |  |  | Zone 15; Actual room temperature [1/100 °C]
| ZoneModule 15 - Supply Temperature Actual Value | °C | 3x2411 |  | AI2410 |  | -4000 | 10000 |  |  | Zone 15; Actual inlet temperature [1/100 °C]
| ZoneModule 15 - Remote Setpoint Offset Actual Value | K | 3x2412 |  | AI2411 |  | -4000 | 10000 |  |  | Zone 15; Actual temperature offset from potentiometer [1/100 °C]
| ZoneModule 15 - CO2/VOC Actual Value | ppm | 3x2413 |  | AI2412 |  | 0 | 5000 |  |  | Zone 15; Actual CO2/VOC level [ppm]
| ZoneModule 15 - RH Actual Value | rh | 3x2414 |  | AI2413 |  | 0 | 10000 |  |  | Zone 15; Actual relative humidity level [%rh]
| ZoneModule 15 - Room Temperature Actual Setpoint | °C | 3x2415 |  | AI2414 |  | -4000 | 10000 |  |  | Zone 15; Actual controller setpoint, room temperature [1/100 °C]
| ZoneModule 15 - Room Panel Air Mode |  | 3x2416 | 3.30 | AI2415 | 3.30 | 0 | 3 |  |  | Zone 15; RPT-20 Room Panel; Actual Air Mode: 0 = Auto 1 = Low 2 = High 3 = Stop
| ZoneModule 15 - Heating Valve Actual Flow | l/h | 3x2417 | 3.30 | AI2416 | 3.30 | 0 | 65535 |  |  | Zone 15; Actual Flow; Heating Valve [l/h]
| ZoneModule 15 - Cooling Valve Actual Flow | l/h | 3x2418 | 3.30 | AI2417 | 3.30 | 0 | 65535 |  |  | Zone 15; Actual Flow; Cooling Valve [l/h]
| ZoneModule 15 - VAV Supply 1 Actual Damper pos. % | % | 3x2419 | 3.30 | AI2418 | 3.30 | 0 | 10000 |  |  | Zone 15; Actual setpoint; VAV Supply 1 damper no. 1 [1/100 %]
| ZoneModule 15 - VAV Supply 2 Actual Damper pos. % | % | 3x2420 | 3.30 | AI2419 | 3.30 | 0 | 10000 |  |  | Zone 15; Actual air quantity;VAV Supply 1 damper no. 1 [m3/h]
| ZoneModule 15 - VAV Extract Actual Damper pos. % | % | 3x2421 | 3.30 | AI2420 | 3.30 | 0 | 10000 |  |  | Zone 15; Actual position; VAV Extract 1 damper no. 1 [1/100 %]
| ZoneModule 15 - EL Heater 1 Temp. Sensor Value | °C | 3x2422 | 3.40 | AI2421 | 3.40 | -4000 | 10000 |  |  | Zone 15; Electric heating Coil 1; Sensor Temperature [1/100 °C]
| ZoneModule 15 - EL Heater 2 Temp. Sensor Value | °C | 3x2423 | 3.40 | AI2422 | 3.40 | -4000 | 10000 |  |  | Zone 15; Electric heating Coil 2; Sensor Temperature [1/100 °C]
| ZoneModule 15 - Ext Aout1 Output | % | 3x2424 | 3.40 | AI2423 | 3.40 | 0 | 10000 |  |  | Zone 15; Extension Module; Actual value Analog Output Aout1 [1/100 V]
| ZoneModule 15 - Ext Aout2 Output | % | 3x2425 | 3.40 | AI2424 | 3.40 | 0 | 10000 |  |  | Zone 15; Extension Module; Actual value Analog Output Aout2 [1/100 V]
| ZoneModule 15 - ZoneModule Alarm Bitmap 1 |  | 3x2426 | 3.40 | AI2425 | 3.40 | 0 | 65535 |  |  | Zone 15; Alarm Bit Map 1 - see tab below: Bit Map Alarm Overview
| ZoneModule 15 - ZoneModule Alarm Bitmap 2 |  | 3x2427 | 3.40 | AI2426 | 3.40 | 0 | 65535 |  |  | Zone 15; Alarm Bit Map 2 - see tab below: Bit Map Alarm Overview
| ZoneModule 15 - ZoneModule Alarm Bitmap 3 |  | 3x2428 | 3.40 | AI2427 | 3.40 | 0 | 65535 |  |  | Zone 15; Alarm Bit Map 3 - see tab below: Bit Map Alarm Overview
| ZoneModule 15 - ZoneModule Alarm Bitmap 4 |  | 3x2429 | 3.40 | AI2428 | 3.40 | 0 | 65535 |  |  | Zone 15; Alarm Bit Map 4 - see tab below: Bit Map Alarm Overview
| ZoneModule 15 - VAV Extract 2 Actuator Setpoint % | % | 3x2430 | 3.40 | AI2429 | 3.40 | 0 | 10000 |  |  | Zone 15; Actual setpoint; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 15 - VAV Extract 2 Actual Flow | m3/h | 3x2431 | 3.40 | AI2430 | 3.40 | 0 | 65535 |  |  | Zone 15; Actual air quantity;VAV Extract 2 damper no. 1 [m3/h]
| ZoneModule 15 - VAV Extract 2 Actual Damper pos. % | % | 3x2432 | 3.40 | AI2431 | 3.40 | 0 | 10000 |  |  | Zone 15; Actual position; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 16 - Status |  | 3x2501 |  | AI2500 |  | 0 | 2 |  |  | Actual status, Zone 16: 0 = Normal 1 = B-alarm 2 = A-alarm
| ZoneModule 16 - VAV Supply 1 Actuator Setpoint % | % | 3x2502 |  | AI2501 |  | 0 | 10000 |  |  | Zone 16; Actual setpoint; VAV inlet damper no. 1 [1/100 %]
| ZoneModule 16 - VAV Supply 1 Actual Flow | m3/h | 3x2503 |  | AI2502 |  | 0 | 65535 |  |  | Zone 16; Actual air quantity; VAV inlet damper no. 1 [m3/h]
| ZoneModule 16 - VAV Supply 2 Actuator Setpoint % | % | 3x2504 |  | AI2503 |  | 0 | 10000 |  |  | Zone 16; Actual setpoint; VAV inlet damper no. 2 [1/100 %]
| ZoneModule 16 - VAV Supply 2 Actual Flow | m3/h | 3x2505 |  | AI2504 |  | 0 | 65535 |  |  | Zone 16; Actual air quantity; VAV inlet damper no. 2 [m3/h]
| ZoneModule 16 - VAV Extract Actuator Setpoint % | % | 3x2506 |  | AI2505 |  | 0 | 10000 |  |  | Zone 16; Actual setpoint; VAV exhaust damper [1/100 %]
| ZoneModule 16 - VAV Extract Actual Flow | m3/h | 3x2507 |  | AI2506 |  | 0 | 65535 |  |  | Zone 16; Actual air quantity; VAV exhaust damper [m3/h]
| ZoneModule 16 - Heating Valve Setpoint % | % | 3x2508 |  | AI2507 |  | 0 | 10000 |  |  | Zone 16; Actual opening, heating valve [1/100 %]
| ZoneModule 16 - Cooling Valve Setpoint % | % | 3x2509 |  | AI2508 |  | 0 | 10000 |  |  | Zone 16; Actual opening, cooling valve [1/100 %]
| ZoneModule 16 - Room Temperature Actual Value | °C | 3x2510 |  | AI2509 |  | -4000 | 10000 |  |  | Zone 16; Actual room temperature [1/100 °C]
| ZoneModule 16 - Supply Temperature Actual Value | °C | 3x2511 |  | AI2510 |  | -4000 | 10000 |  |  | Zone 16; Actual inlet temperature [1/100 °C]
| ZoneModule 16 - Remote Setpoint Offset Actual Value | K | 3x2512 |  | AI2511 |  | -4000 | 10000 |  |  | Zone 16; Actual temperature offset from potentiometer [1/100 °C]
| ZoneModule 16 - CO2/VOC Actual Value | ppm | 3x2513 |  | AI2512 |  | 0 | 5000 |  |  | Zone 16; Actual CO2/VOC level [ppm]
| ZoneModule 16 - RH Actual Value | rh | 3x2514 |  | AI2513 |  | 0 | 10000 |  |  | Zone 16; Actual relative humidity level [%rh]
| ZoneModule 16 - Room Temperature Actual Setpoint | °C | 3x2515 |  | AI2514 |  | -4000 | 10000 |  |  | Zone 16; Actual controller setpoint, room temperature [1/100 °C]
| ZoneModule 16 - Room Panel Air Mode |  | 3x2516 | 3.30 | AI2515 | 3.30 | 0 | 3 |  |  | Zone 16; RPT-20 Room Panel; Actual Air Mode: 0 = Auto 1 = Low 2 = High 3 = Stop
| ZoneModule 16 - Heating Valve Actual Flow | l/h | 3x2517 | 3.30 | AI2516 | 3.30 | 0 | 65535 |  |  | Zone 16; Actual Flow; Heating Valve [l/h]
| ZoneModule 16 - Cooling Valve Actual Flow | l/h | 3x2518 | 3.30 | AI2517 | 3.30 | 0 | 65535 |  |  | Zone 16; Actual Flow; Cooling Valve [l/h]
| ZoneModule 16 - VAV Supply 1 Actual Damper pos. % | % | 3x2519 | 3.30 | AI2518 | 3.30 | 0 | 10000 |  |  | Zone 16; Actual setpoint; VAV Supply 1 damper no. 1 [1/100 %]
| ZoneModule 16 - VAV Supply 2 Actual Damper pos. % | % | 3x2520 | 3.30 | AI2519 | 3.30 | 0 | 10000 |  |  | Zone 16; Actual air quantity;VAV Supply 1 damper no. 1 [m3/h]
0x2320 | ZoneModule 16 - VAV Extract Actual Damper pos. % | % | 3x2521 | 3.30 | AI2520 | 3.30 | 0 | 10000 |  |  | Zone 16; Actual position; VAV Extract 1 damper no. 1 [1/100 %]
0x2460 | ZoneModule 16 - EL Heater 1 Temp. Sensor Value | °C | 3x2522 | 3.40 | AI2521 | 3.40 | -4000 | 10000 |  |  | Zone 16; Electric heating Coil 1; Sensor Temperature [1/100 °C]
0x2461 | ZoneModule 16 - EL Heater 2 Temp. Sensor Value | °C | 3x2523 | 3.40 | AI2522 | 3.40 | -4000 | 10000 |  |  | Zone 16; Electric heating Coil 2; Sensor Temperature [1/100 °C]
0x2920 | ZoneModule 16 - Ext Aout1 Output | % | 3x2524 | 3.40 | AI2523 | 3.40 | 0 | 10000 |  |  | Zone 16; Extension Module; Actual value Analog Output Aout1 [1/100 V]
0x2330 | ZoneModule 16 - Ext Aout2 Output | % | 3x2525 | 3.40 | AI2524 | 3.40 | 0 | 10000 |  |  | Zone 16; Extension Module; Actual value Analog Output Aout2 [1/100 V]
0x2121 | ZoneModule 16 - ZoneModule Alarm Bitmap 1 |  | 3x2526 | 3.40 | AI2525 | 3.40 | 0 | 65535 |  |  | Zone 16; Alarm Bit Map 1 - see tab below: Bit Map Alarm Overview
0x2221 | ZoneModule 16 - ZoneModule Alarm Bitmap 2 |  | 3x2527 | 3.40 | AI2526 | 3.40 | 0 | 65535 |  |  | Zone 16; Alarm Bit Map 2 - see tab below: Bit Map Alarm Overview
0x239A | ZoneModule 16 - ZoneModule Alarm Bitmap 3 |  | 3x2528 | 3.40 | AI2527 | 3.40 | 0 | 65535 |  |  | Zone 16; Alarm Bit Map 3 - see tab below: Bit Map Alarm Overview
0x2160 | ZoneModule 16 - ZoneModule Alarm Bitmap 4 |  | 3x2529 | 3.40 | AI2528 | 3.40 | 0 | 65535 |  |  | Zone 16; Alarm Bit Map 4 - see tab below: Bit Map Alarm Overview
0x239B | ZoneModule 16 - VAV Extract 2 Actuator Setpoint % | % | 3x2530 | 3.40 | AI2529 | 3.40 | 0 | 10000 |  |  | Zone 16; Actual setpoint; VAV Extract 2 damper no. 1 [1/100 %]
0x2260 | ZoneModule 16 - VAV Extract 2 Actual Flow | m3/h | 3x2531 | 3.40 | AI2530 | 3.40 | 0 | 65535 |  |  | Zone 16; Actual air quantity;VAV Extract 2 damper no. 1 [m3/h]
0x239C | ZoneModule 16 - VAV Extract 2 Actual Damper pos. % | % | 3x2532 | 3.40 | AI2531 | 3.40 | 0 | 10000 |  |  | Zone 16; Actual position; VAV Extract 2 damper no. 1 [1/100 %]
0x239D | ZoneModule 17 - Status |  | 3x2601 |  | AI2600 |  | 0 | 2 |  |  | Actual status, Zone 17: 0 = Normal 1 = B-alarm 2 = A-alarm
0x2394 | ZoneModule 17 - VAV Supply 1 Actuator Setpoint % | % | 3x2602 |  | AI2601 |  | 0 | 10000 |  |  | Zone 17; Actual setpoint; VAV inlet damper no. 1 [1/100 %]
0x2395 | ZoneModule 17 - VAV Supply 1 Actual Flow | m3/h | 3x2603 |  | AI2602 |  | 0 | 65535 |  |  | Zone 17; Actual air quantity; VAV inlet damper no. 1 [m3/h]
0x236C | ZoneModule 17 - VAV Supply 2 Actuator Setpoint % | % | 3x2604 |  | AI2603 |  | 0 | 10000 |  |  | Zone 17; Actual setpoint; VAV inlet damper no. 2 [1/100 %]
0x2A84 | ZoneModule 17 - VAV Supply 2 Actual Flow | m3/h | 3x2605 |  | AI2604 |  | 0 | 65535 |  |  | Zone 17; Actual air quantity; VAV inlet damper no. 2 [m3/h]
0x2AF4 | ZoneModule 17 - VAV Extract Actuator Setpoint % | % | 3x2606 |  | AI2605 |  | 0 | 10000 |  |  | Zone 17; Actual setpoint; VAV exhaust damper [1/100 %]
0x2AFC | ZoneModule 17 - VAV Extract Actual Flow | m3/h | 3x2607 |  | AI2606 |  | 0 | 65535 |  |  | Zone 17; Actual air quantity; VAV exhaust damper [m3/h]
0x239E | ZoneModule 17 - Heating Valve Setpoint % | % | 3x2608 |  | AI2607 |  | 0 | 10000 |  |  | Zone 17; Actual opening, heating valve [1/100 %]
0x239F | ZoneModule 17 - Cooling Valve Setpoint % | % | 3x2609 |  | AI2608 |  | 0 | 10000 |  |  | Zone 17; Actual opening, cooling valve [1/100 %]
0x2125 | ZoneModule 17 - Room Temperature Actual Value | °C | 3x2610 |  | AI2609 |  | -4000 | 10000 |  |  | Zone 17; Actual room temperature [1/100 °C]
0x2126 | ZoneModule 17 - Supply Temperature Actual Value | °C | 3x2611 |  | AI2610 |  | -4000 | 10000 |  |  | Zone 17; Actual inlet temperature [1/100 °C]
0x23C0 | ZoneModule 17 - Remote Setpoint Offset Actual Value | K | 3x2612 |  | AI2611 |  | -4000 | 10000 |  |  | Zone 17; Actual temperature offset from potentiometer [1/100 °C]
0x2380 | ZoneModule 17 - CO2/VOC Actual Value | ppm | 3x2613 |  | AI2612 |  | 0 | 5000 |  |  | Zone 17; Actual CO2/VOC level [ppm]
0x2370 | ZoneModule 17 - RH Actual Value | rh | 3x2614 |  | AI2613 |  | 0 | 10000 |  |  | Zone 17; Actual relative humidity level [%rh]
0x2400 | ZoneModule 17 - Room Temperature Actual Setpoint | °C | 3x2615 |  | AI2614 |  | -4000 | 10000 |  |  | Zone 17; Actual controller setpoint, room temperature [1/100 °C]
0x2401 | ZoneModule 17 - Room Panel Air Mode |  | 3x2616 | 3.30 | AI2615 | 3.30 | 0 | 3 |  |  | Zone 17; RPT-20 Room Panel; Actual Air Mode: 0 = Auto 1 = Low 2 = High 3 = Stop
0x2420 | ZoneModule 17 - Heating Valve Actual Flow | l/h | 3x2617 | 3.30 | AI2616 | 3.30 | 0 | 65535 |  |  | Zone 17; Actual Flow; Heating Valve [l/h]
0x242A | ZoneModule 17 - Cooling Valve Actual Flow | l/h | 3x2618 | 3.30 | AI2617 | 3.30 | 0 | 65535 |  |  | Zone 17; Actual Flow; Cooling Valve [l/h]
0x2421 | ZoneModule 17 - VAV Supply 1 Actual Damper pos. % | % | 3x2619 | 3.30 | AI2618 | 3.30 | 0 | 10000 |  |  | Zone 17; Actual setpoint; VAV Supply 1 damper no. 1 [1/100 %]
0x2426 | ZoneModule 17 - VAV Supply 2 Actual Damper pos. % | % | 3x2620 | 3.30 | AI2619 | 3.30 | 0 | 10000 |  |  | Zone 17; Actual air quantity;VAV Supply 1 damper no. 1 [m3/h]
0x2427 | ZoneModule 17 - VAV Extract Actual Damper pos. % | % | 3x2621 | 3.30 | AI2620 | 3.30 | 0 | 10000 |  |  | Zone 17; Actual position; VAV Extract 1 damper no. 1 [1/100 %]
0x2428 | ZoneModule 17 - EL Heater 1 Temp. Sensor Value | °C | 3x2622 | 3.40 | AI2621 | 3.40 | -4000 | 10000 |  |  | Zone 17; Electric heating Coil 1; Sensor Temperature [1/100 °C]
0x2429 | ZoneModule 17 - EL Heater 2 Temp. Sensor Value | °C | 3x2623 | 3.40 | AI2622 | 3.40 | -4000 | 10000 |  |  | Zone 17; Electric heating Coil 2; Sensor Temperature [1/100 °C]
0x2500 | ZoneModule 17 - Ext Aout1 Output | % | 3x2624 | 3.40 | AI2623 | 3.40 | 0 | 10000 |  |  | Zone 17; Extension Module; Actual value Analog Output Aout1 [1/100 V]
0x2501 | ZoneModule 17 - Ext Aout2 Output | % | 3x2625 | 3.40 | AI2624 | 3.40 | 0 | 10000 |  |  | Zone 17; Extension Module; Actual value Analog Output Aout2 [1/100 V]
0x2502 | ZoneModule 17 - ZoneModule Alarm Bitmap 1 |  | 3x2626 | 3.40 | AI2625 | 3.40 | 0 | 65535 |  |  | Zone 17; Alarm Bit Map 1 - see tab below: Bit Map Alarm Overview
0x2503 | ZoneModule 17 - ZoneModule Alarm Bitmap 2 |  | 3x2627 | 3.40 | AI2626 | 3.40 | 0 | 65535 |  |  | Zone 17; Alarm Bit Map 2 - see tab below: Bit Map Alarm Overview
0x2408 | ZoneModule 17 - ZoneModule Alarm Bitmap 3 |  | 3x2628 | 3.40 | AI2627 | 3.40 | 0 | 65535 |  |  | Zone 17; Alarm Bit Map 3 - see tab below: Bit Map Alarm Overview
0x2A30 | ZoneModule 17 - ZoneModule Alarm Bitmap 4 |  | 3x2629 | 3.40 | AI2628 | 3.40 | 0 | 65535 |  |  | Zone 17; Alarm Bit Map 4 - see tab below: Bit Map Alarm Overview
0x2A31 | ZoneModule 17 - VAV Extract 2 Actuator Setpoint % | % | 3x2630 | 3.40 | AI2629 | 3.40 | 0 | 10000 |  |  | Zone 17; Actual setpoint; VAV Extract 2 damper no. 1 [1/100 %]
0x2A32 | ZoneModule 17 - VAV Extract 2 Actual Flow | m3/h | 3x2631 | 3.40 | AI2630 | 3.40 | 0 | 65535 |  |  | Zone 17; Actual air quantity;VAV Extract 2 damper no. 1 [m3/h]
0x2A33 | ZoneModule 17 - VAV Extract 2 Actual Damper pos. % | % | 3x2632 | 3.40 | AI2631 | 3.40 | 0 | 10000 |  |  | Zone 17; Actual position; VAV Extract 2 damper no. 1 [1/100 %]
0x2A34 | ZoneModule 18 - Status |  | 3x2701 |  | AI2700 |  | 0 | 2 |  |  | Actual status, Zone 18: 0 = Normal 1 = B-alarm 2 = A-alarm
0x2A37 | ZoneModule 18 - VAV Supply 1 Actuator Setpoint % | % | 3x2702 |  | AI2701 |  | 0 | 10000 |  |  | Zone 18; Actual setpoint; VAV inlet damper no. 1 [1/100 %]
0x2A38 | ZoneModule 18 - VAV Supply 1 Actual Flow | m3/h | 3x2703 |  | AI2702 |  | 0 | 65535 |  |  | Zone 18; Actual air quantity; VAV inlet damper no. 1 [m3/h]
0x2A3A | ZoneModule 18 - VAV Supply 2 Actuator Setpoint % | % | 3x2704 |  | AI2703 |  | 0 | 10000 |  |  | Zone 18; Actual setpoint; VAV inlet damper no. 2 [1/100 %]
0x2143 | ZoneModule 18 - VAV Supply 2 Actual Flow | m3/h | 3x2705 |  | AI2704 |  | 0 | 65535 |  |  | Zone 18; Actual air quantity; VAV inlet damper no. 2 [m3/h]
0x2A50 | ZoneModule 18 - VAV Extract Actuator Setpoint % | % | 3x2706 |  | AI2705 |  | 0 | 10000 |  |  | Zone 18; Actual setpoint; VAV exhaust damper [1/100 %]
0x2A51 | ZoneModule 18 - VAV Extract Actual Flow | m3/h | 3x2707 |  | AI2706 |  | 0 | 65535 |  |  | Zone 18; Actual air quantity; VAV exhaust damper [m3/h]
0x2A52 | ZoneModule 18 - Heating Valve Setpoint % | % | 3x2708 |  | AI2707 |  | 0 | 10000 |  |  | Zone 18; Actual opening, heating valve [1/100 %]
0x2A53 | ZoneModule 18 - Cooling Valve Setpoint % | % | 3x2709 |  | AI2708 |  | 0 | 10000 |  |  | Zone 18; Actual opening, cooling valve [1/100 %]
0x2A54 | ZoneModule 18 - Room Temperature Actual Value | °C | 3x2710 |  | AI2709 |  | -4000 | 10000 |  |  | Zone 18; Actual room temperature [1/100 °C]
0x2A57 | ZoneModule 18 - Supply Temperature Actual Value | °C | 3x2711 |  | AI2710 |  | -4000 | 10000 |  |  | Zone 18; Actual inlet temperature [1/100 °C]
0x2A58 | ZoneModule 18 - Remote Setpoint Offset Actual Value | K | 3x2712 |  | AI2711 |  | -4000 | 10000 |  |  | Zone 18; Actual temperature offset from potentiometer [1/100 °C]
0x2A5A | ZoneModule 18 - CO2/VOC Actual Value | ppm | 3x2713 |  | AI2712 |  | 0 | 5000 |  |  | Zone 18; Actual CO2/VOC level [ppm]
0x2243 | ZoneModule 18 - RH Actual Value | rh | 3x2714 |  | AI2713 |  | 0 | 10000 |  |  | Zone 18; Actual relative humidity level [%rh]
0x2A70 | ZoneModule 18 - Room Temperature Actual Setpoint | °C | 3x2715 |  | AI2714 |  | -4000 | 10000 |  |  | Zone 18; Actual controller setpoint, room temperature [1/100 °C]
0x2A71 | ZoneModule 18 - Room Panel Air Mode |  | 3x2716 | 3.30 | AI2715 | 3.30 | 0 | 3 |  |  | Zone 18; RPT-20 Room Panel; Actual Air Mode: 0 = Auto 1 = Low 2 = High 3 = Stop
0x2A72 | ZoneModule 18 - Heating Valve Actual Flow | l/h | 3x2717 | 3.30 | AI2716 | 3.30 | 0 | 65535 |  |  | Zone 18; Actual Flow; Heating Valve [l/h]
0x2A74 | ZoneModule 18 - Cooling Valve Actual Flow | l/h | 3x2718 | 3.30 | AI2717 | 3.30 | 0 | 65535 |  |  | Zone 18; Actual Flow; Cooling Valve [l/h]
0x2A76 | ZoneModule 18 - VAV Supply 1 Actual Damper pos. % | % | 3x2719 | 3.30 | AI2718 | 3.30 | 0 | 10000 |  |  | Zone 18; Actual setpoint; VAV Supply 1 damper no. 1 [1/100 %]
0x2A77 | ZoneModule 18 - VAV Supply 2 Actual Damper pos. % | % | 3x2720 | 3.30 | AI2719 | 3.30 | 0 | 10000 |  |  | Zone 18; Actual air quantity;VAV Supply 1 damper no. 1 [m3/h]
0x2A79 | ZoneModule 18 - VAV Extract Actual Damper pos. % | % | 3x2721 | 3.30 | AI2720 | 3.30 | 0 | 10000 |  |  | Zone 18; Actual position; VAV Extract 1 damper no. 1 [1/100 %]
0x2A7A | ZoneModule 18 - EL Heater 1 Temp. Sensor Value | °C | 3x2722 | 3.40 | AI2721 | 3.40 | -4000 | 10000 |  |  | Zone 18; Electric heating Coil 1; Sensor Temperature [1/100 °C]
0x2A90 | ZoneModule 18 - EL Heater 2 Temp. Sensor Value | °C | 3x2723 | 3.40 | AI2722 | 3.40 | -4000 | 10000 |  |  | Zone 18; Electric heating Coil 2; Sensor Temperature [1/100 °C]
0x2AB0 | ZoneModule 18 - Ext Aout1 Output | % | 3x2724 | 3.40 | AI2723 | 3.40 | 0 | 10000 |  |  | Zone 18; Extension Module; Actual value Analog Output Aout1 [1/100 V]
0x2411 | ZoneModule 18 - Ext Aout2 Output | % | 3x2725 | 3.40 | AI2724 | 3.40 | 0 | 10000 |  |  | Zone 18; Extension Module; Actual value Analog Output Aout2 [1/100 V]
0x2413 | ZoneModule 18 - ZoneModule Alarm Bitmap 1 |  | 3x2726 | 3.40 | AI2725 | 3.40 | 0 | 65535 |  |  | Zone 18; Alarm Bit Map 1 - see tab below: Bit Map Alarm Overview
0x2800 | ZoneModule 18 - ZoneModule Alarm Bitmap 2 |  | 3x2727 | 3.40 | AI2726 | 3.40 | 0 | 65535 |  |  | Zone 18; Alarm Bit Map 2 - see tab below: Bit Map Alarm Overview
0x2808 | ZoneModule 18 - ZoneModule Alarm Bitmap 3 |  | 3x2728 | 3.40 | AI2727 | 3.40 | 0 | 65535 |  |  | Zone 18; Alarm Bit Map 3 - see tab below: Bit Map Alarm Overview
0x2809 | ZoneModule 18 - ZoneModule Alarm Bitmap 4 |  | 3x2729 | 3.40 | AI2728 | 3.40 | 0 | 65535 |  |  | Zone 18; Alarm Bit Map 4 - see tab below: Bit Map Alarm Overview
0x236E | ZoneModule 18 - VAV Extract 2 Actuator Setpoint % | % | 3x2730 | 3.40 | AI2729 | 3.40 | 0 | 10000 |  |  | Zone 18; Actual setpoint; VAV Extract 2 damper no. 1 [1/100 %]
0x2E10 | ZoneModule 18 - VAV Extract 2 Actual Flow | m3/h | 3x2731 | 3.40 | AI2730 | 3.40 | 0 | 65535 |  |  | Zone 18; Actual air quantity;VAV Extract 2 damper no. 1 [m3/h]
0x2E11 | ZoneModule 18 - VAV Extract 2 Actual Damper pos. % | % | 3x2732 | 3.40 | AI2731 | 3.40 | 0 | 10000 |  |  | Zone 18; Actual position; VAV Extract 2 damper no. 1 [1/100 %]
0x2E12 | ZoneModule 19 - Status |  | 3x2801 |  | AI2800 |  | 0 | 2 |  |  | Actual status, Zone 19: 0 = Normal 1 = B-alarm 2 = A-alarm
0x2E13 | ZoneModule 19 - VAV Supply 1 Actuator Setpoint % | % | 3x2802 |  | AI2801 |  | 0 | 10000 |  |  | Zone 19; Actual setpoint; VAV inlet damper no. 1 [1/100 %]
0x2E14 | ZoneModule 19 - VAV Supply 1 Actual Flow | m3/h | 3x2803 |  | AI2802 |  | 0 | 65535 |  |  | Zone 19; Actual air quantity; VAV inlet damper no. 1 [m3/h]
0x2E15 | ZoneModule 19 - VAV Supply 2 Actuator Setpoint % | % | 3x2804 |  | AI2803 |  | 0 | 10000 |  |  | Zone 19; Actual setpoint; VAV inlet damper no. 2 [1/100 %]
0x2E16 | ZoneModule 19 - VAV Supply 2 Actual Flow | m3/h | 3x2805 |  | AI2804 |  | 0 | 65535 |  |  | Zone 19; Actual air quantity; VAV inlet damper no. 2 [m3/h]
0x2E17 | ZoneModule 19 - VAV Extract Actuator Setpoint % | % | 3x2806 |  | AI2805 |  | 0 | 10000 |  |  | Zone 19; Actual setpoint; VAV exhaust damper [1/100 %]
0x2E18 | ZoneModule 19 - VAV Extract Actual Flow | m3/h | 3x2807 |  | AI2806 |  | 0 | 65535 |  |  | Zone 19; Actual air quantity; VAV exhaust damper [m3/h]
0x2E19 | ZoneModule 19 - Heating Valve Setpoint % | % | 3x2808 |  | AI2807 |  | 0 | 10000 |  |  | Zone 19; Actual opening, heating valve [1/100 %]
0x2E1A | ZoneModule 19 - Cooling Valve Setpoint % | % | 3x2809 |  | AI2808 |  | 0 | 10000 |  |  | Zone 19; Actual opening, cooling valve [1/100 %]
0x2E1B | ZoneModule 19 - Room Temperature Actual Value | °C | 3x2810 |  | AI2809 |  | -4000 | 10000 |  |  | Zone 19; Actual room temperature [1/100 °C]
0x2E1C | ZoneModule 19 - Supply Temperature Actual Value | °C | 3x2811 |  | AI2810 |  | -4000 | 10000 |  |  | Zone 19; Actual inlet temperature [1/100 °C]
0x2E1D | ZoneModule 19 - Remote Setpoint Offset Actual Value | K | 3x2812 |  | AI2811 |  | -4000 | 10000 |  |  | Zone 19; Actual temperature offset from potentiometer [1/100 °C]
0x2E1E | ZoneModule 19 - CO2/VOC Actual Value | ppm | 3x2813 |  | AI2812 |  | 0 | 5000 |  |  | Zone 19; Actual CO2/VOC level [ppm]
0x2E1F | ZoneModule 19 - RH Actual Value | rh | 3x2814 |  | AI2813 |  | 0 | 10000 |  |  | Zone 19; Actual relative humidity level [%rh]
0x2000 | ZoneModule 19 - Room Temperature Actual Setpoint | °C | 3x2815 |  | AI2814 |  | -4000 | 10000 |  |  | Zone 19; Actual controller setpoint, room temperature [1/100 °C]
0x2001 | ZoneModule 19 - Room Panel Air Mode |  | 3x2816 | 3.30 | AI2815 | 3.30 | 0 | 3 |  |  | Zone 19; RPT-20 Room Panel; Actual Air Mode: 0 = Auto 1 = Low 2 = High 3 = Stop
0x1ED0 | ZoneModule 19 - Heating Valve Actual Flow | l/h | 3x2817 | 3.30 | AI2816 | 3.30 | 0 | 65535 |  |  | Zone 19; Actual Flow; Heating Valve [l/h]
0x1ED1 | ZoneModule 19 - Cooling Valve Actual Flow | l/h | 3x2818 | 3.30 | AI2817 | 3.30 | 0 | 65535 |  |  | Zone 19; Actual Flow; Cooling Valve [l/h]
0x1ED2 | ZoneModule 19 - VAV Supply 1 Actual Damper pos. % | % | 3x2819 | 3.30 | AI2818 | 3.30 | 0 | 10000 |  |  | Zone 19; Actual setpoint; VAV Supply 1 damper no. 1 [1/100 %]
0x2360 | ZoneModule 19 - VAV Supply 2 Actual Damper pos. % | % | 3x2820 | 3.30 | AI2819 | 3.30 | 0 | 10000 |  |  | Zone 19; Actual air quantity;VAV Supply 1 damper no. 1 [m3/h]
0x2361 | ZoneModule 19 - VAV Extract Actual Damper pos. % | % | 3x2821 | 3.30 | AI2820 | 3.30 | 0 | 10000 |  |  | Zone 19; Actual position; VAV Extract 1 damper no. 1 [1/100 %]
0x2362 | ZoneModule 19 - EL Heater 1 Temp. Sensor Value | °C | 3x2822 | 3.40 | AI2821 | 3.40 | -4000 | 10000 |  |  | Zone 19; Electric heating Coil 1; Sensor Temperature [1/100 °C]
0x2363 | ZoneModule 19 - EL Heater 2 Temp. Sensor Value | °C | 3x2823 | 3.40 | AI2822 | 3.40 | -4000 | 10000 |  |  | Zone 19; Electric heating Coil 2; Sensor Temperature [1/100 °C]
0x2364 | ZoneModule 19 - Ext Aout1 Output | % | 3x2824 | 3.40 | AI2823 | 3.40 | 0 | 10000 |  |  | Zone 19; Extension Module; Actual value Analog Output Aout1 [1/100 V]
0x23A0 | ZoneModule 19 - Ext Aout2 Output | % | 3x2825 | 3.40 | AI2824 | 3.40 | 0 | 10000 |  |  | Zone 19; Extension Module; Actual value Analog Output Aout2 [1/100 V]
0x2366 | ZoneModule 19 - ZoneModule Alarm Bitmap 1 |  | 3x2826 | 3.40 | AI2825 | 3.40 | 0 | 65535 |  |  | Zone 19; Alarm Bit Map 1 - see tab below: Bit Map Alarm Overview
0x2367 | ZoneModule 19 - ZoneModule Alarm Bitmap 2 |  | 3x2827 | 3.40 | AI2826 | 3.40 | 0 | 65535 |  |  | Zone 19; Alarm Bit Map 2 - see tab below: Bit Map Alarm Overview
0x2368 | ZoneModule 19 - ZoneModule Alarm Bitmap 3 |  | 3x2828 | 3.40 | AI2827 | 3.40 | 0 | 65535 |  |  | Zone 19; Alarm Bit Map 3 - see tab below: Bit Map Alarm Overview
0x2369 | ZoneModule 19 - ZoneModule Alarm Bitmap 4 |  | 3x2829 | 3.40 | AI2828 | 3.40 | 0 | 65535 |  |  | Zone 19; Alarm Bit Map 4 - see tab below: Bit Map Alarm Overview
0x236A | ZoneModule 19 - VAV Extract 2 Actuator Setpoint % | % | 3x2830 | 3.40 | AI2829 | 3.40 | 0 | 10000 |  |  | Zone 19; Actual setpoint; VAV Extract 2 damper no. 1 [1/100 %]
0x236B | ZoneModule 19 - VAV Extract 2 Actual Flow | m3/h | 3x2831 | 3.40 | AI2830 | 3.40 | 0 | 65535 |  |  | Zone 19; Actual air quantity;VAV Extract 2 damper no. 1 [m3/h]
0x2390 | ZoneModule 19 - VAV Extract 2 Actual Damper pos. % | % | 3x2832 | 3.40 | AI2831 | 3.40 | 0 | 10000 |  |  | Zone 19; Actual position; VAV Extract 2 damper no. 1 [1/100 %]
0x2391 | ZoneModule 20 - Status |  | 3x2901 |  | AI2900 |  | 0 | 2 |  |  | Actual status, Zone 20: 0 = Normal 1 = B-alarm 2 = A-alarm
0x2392 | ZoneModule 20 - VAV Supply 1 Actuator Setpoint % | % | 3x2902 |  | AI2901 |  | 0 | 10000 |  |  | Zone 20; Actual setpoint; VAV inlet damper no. 1 [1/100 %]
0x2393 | ZoneModule 20 - VAV Supply 1 Actual Flow | m3/h | 3x2903 |  | AI2902 |  | 0 | 65535 |  |  | Zone 20; Actual air quantity; VAV inlet damper no. 1 [m3/h]
0x2110 | ZoneModule 20 - VAV Supply 2 Actuator Setpoint % | % | 3x2904 |  | AI2903 |  | 0 | 10000 |  |  | Zone 20; Actual setpoint; VAV inlet damper no. 2 [1/100 %]
0x2111 | ZoneModule 20 - VAV Supply 2 Actual Flow | m3/h | 3x2905 |  | AI2904 |  | 0 | 65535 |  |  | Zone 20; Actual air quantity; VAV inlet damper no. 2 [m3/h]
0x2112 | ZoneModule 20 - VAV Extract Actuator Setpoint % | % | 3x2906 |  | AI2905 |  | 0 | 10000 |  |  | Zone 20; Actual setpoint; VAV exhaust damper [1/100 %]
0x2113 | ZoneModule 20 - VAV Extract Actual Flow | m3/h | 3x2907 |  | AI2906 |  | 0 | 65535 |  |  | Zone 20; Actual air quantity; VAV exhaust damper [m3/h]
0x2441 | ZoneModule 20 - Heating Valve Setpoint % | % | 3x2908 |  | AI2907 |  | 0 | 10000 |  |  | Zone 20; Actual opening, heating valve [1/100 %]
0x2442 | ZoneModule 20 - Cooling Valve Setpoint % | % | 3x2909 |  | AI2908 |  | 0 | 10000 |  |  | Zone 20; Actual opening, cooling valve [1/100 %]
0x240F | ZoneModule 20 - Room Temperature Actual Value | °C | 3x2910 |  | AI2909 |  | -4000 | 10000 |  |  | Zone 20; Actual room temperature [1/100 °C]
0x23AF | ZoneModule 20 - Supply Temperature Actual Value | °C | 3x2911 |  | AI2910 |  | -4000 | 10000 |  |  | Zone 20; Actual inlet temperature [1/100 °C]
0x240E | ZoneModule 20 - Remote Setpoint Offset Actual Value | K | 3x2912 |  | AI2911 |  | -4000 | 10000 |  |  | Zone 20; Actual temperature offset from potentiometer [1/100 °C]
0x23AE | ZoneModule 20 - CO2/VOC Actual Value | ppm | 3x2913 |  | AI2912 |  | 0 | 5000 |  |  | Zone 20; Actual CO2/VOC level [ppm]
0x2479 | ZoneModule 20 - RH Actual Value | rh | 3x2914 |  | AI2913 |  | 0 | 10000 |  |  | Zone 20; Actual relative humidity level [%rh]
0x247A | ZoneModule 20 - Room Temperature Actual Setpoint | °C | 3x2915 |  | AI2914 |  | -4000 | 10000 |  |  | Zone 20; Actual controller setpoint, room temperature [1/100 °C]
0x247B | ZoneModule 20 - Room Panel Air Mode |  | 3x2916 | 3.30 | AI2915 | 3.30 | 0 | 3 |  |  | Zone 20; RPT-20 Room Panel; Actual Air Mode: 0 = Auto 1 = Low 2 = High 3 = Stop
0x2418 | ZoneModule 20 - Heating Valve Actual Flow | l/h | 3x2917 | 3.30 | AI2916 | 3.30 | 0 | 65535 |  |  | Zone 20; Actual Flow; Heating Valve [l/h]
0x24F1 | ZoneModule 20 - Cooling Valve Actual Flow | l/h | 3x2918 | 3.30 | AI2917 | 3.30 | 0 | 65535 |  |  | Zone 20; Actual Flow; Cooling Valve [l/h]
0x24F2 | ZoneModule 20 - VAV Supply 1 Actual Damper pos. % | % | 3x2919 | 3.30 | AI2918 | 3.30 | 0 | 10000 |  |  | Zone 20; Actual setpoint; VAV Supply 1 damper no. 1 [1/100 %]
0x24F0 | ZoneModule 20 - VAV Supply 2 Actual Damper pos. % | % | 3x2920 | 3.30 | AI2919 | 3.30 | 0 | 10000 |  |  | Zone 20; Actual air quantity;VAV Supply 1 damper no. 1 [m3/h]
0x2A85 | ZoneModule 20 - VAV Extract Actual Damper pos. % | % | 3x2921 | 3.30 | AI2920 | 3.30 | 0 | 10000 |  |  | Zone 20; Actual position; VAV Extract 1 damper no. 1 [1/100 %]
0x240A | ZoneModule 20 - EL Heater 1 Temp. Sensor Value | °C | 3x2922 | 3.40 | AI2921 | 3.40 | -4000 | 10000 |  |  | Zone 20; Electric heating Coil 1; Sensor Temperature [1/100 °C]
0x240B | ZoneModule 20 - EL Heater 2 Temp. Sensor Value | °C | 3x2923 | 3.40 | AI2922 | 3.40 | -4000 | 10000 |  |  | Zone 20; Electric heating Coil 2; Sensor Temperature [1/100 °C]
0x240C | ZoneModule 20 - Ext Aout1 Output | % | 3x2924 | 3.40 | AI2923 | 3.40 | 0 | 10000 |  |  | Zone 20; Extension Module; Actual value Analog Output Aout1 [1/100 V]
0x240D | ZoneModule 20 - Ext Aout2 Output | % | 3x2925 | 3.40 | AI2924 | 3.40 | 0 | 10000 |  |  | Zone 20; Extension Module; Actual value Analog Output Aout2 [1/100 V]
0x2980 | ZoneModule 20 - ZoneModule Alarm Bitmap 1 |  | 3x2926 | 3.40 | AI2925 | 3.40 | 0 | 65535 |  |  | Zone 20; Alarm Bit Map 1 - see tab below: Bit Map Alarm Overview
0x2981 | ZoneModule 20 - ZoneModule Alarm Bitmap 2 |  | 3x2927 | 3.40 | AI2926 | 3.40 | 0 | 65535 |  |  | Zone 20; Alarm Bit Map 2 - see tab below: Bit Map Alarm Overview
0x2982 | ZoneModule 20 - ZoneModule Alarm Bitmap 3 |  | 3x2928 | 3.40 | AI2927 | 3.40 | 0 | 65535 |  |  | Zone 20; Alarm Bit Map 3 - see tab below: Bit Map Alarm Overview
0x2983 | ZoneModule 20 - ZoneModule Alarm Bitmap 4 |  | 3x2929 | 3.40 | AI2928 | 3.40 | 0 | 65535 |  |  | Zone 20; Alarm Bit Map 4 - see tab below: Bit Map Alarm Overview
0x2984 | ZoneModule 20 - VAV Extract 2 Actuator Setpoint % | % | 3x2930 | 3.40 | AI2929 | 3.40 | 0 | 10000 |  |  | Zone 20; Actual setpoint; VAV Extract 2 damper no. 1 [1/100 %]
0x2987 | ZoneModule 20 - VAV Extract 2 Actual Flow | m3/h | 3x2931 | 3.40 | AI2930 | 3.40 | 0 | 65535 |  |  | Zone 20; Actual air quantity;VAV Extract 2 damper no. 1 [m3/h]
0x2988 | ZoneModule 20 - VAV Extract 2 Actual Damper pos. % | % | 3x2932 | 3.40 | AI2931 | 3.40 | 0 | 10000 |  |  | Zone 20; Actual position; VAV Extract 2 damper no. 1 [1/100 %]
0x298A | ZoneModule 21 - Status |  | 3x3001 |  | AI3000 |  | 0 | 2 |  |  | Actual status, Zone 21: 0 = Normal 1 = B-alarm 2 = A-alarm
0x298B | ZoneModule 21 - VAV Supply 1 Actuator Setpoint % | % | 3x3002 |  | AI3001 |  | 0 | 10000 |  |  | Zone 21; Actual setpoint; VAV inlet damper no. 1 [1/100 %]
0x298C | ZoneModule 21 - VAV Supply 1 Actual Flow | m3/h | 3x3003 |  | AI3002 |  | 0 | 65535 |  |  | Zone 21; Actual air quantity; VAV inlet damper no. 1 [m3/h]
0x2990 | ZoneModule 21 - VAV Supply 2 Actuator Setpoint % | % | 3x3004 |  | AI3003 |  | 0 | 10000 |  |  | Zone 21; Actual setpoint; VAV inlet damper no. 2 [1/100 %]
0x2991 | ZoneModule 21 - VAV Supply 2 Actual Flow | m3/h | 3x3005 |  | AI3004 |  | 0 | 65535 |  |  | Zone 21; Actual air quantity; VAV inlet damper no. 2 [m3/h]
0x2992 | ZoneModule 21 - VAV Extract Actuator Setpoint % | % | 3x3006 |  | AI3005 |  | 0 | 10000 |  |  | Zone 21; Actual setpoint; VAV exhaust damper [1/100 %]
0x2993 | ZoneModule 21 - VAV Extract Actual Flow | m3/h | 3x3007 |  | AI3006 |  | 0 | 65535 |  |  | Zone 21; Actual air quantity; VAV exhaust damper [m3/h]
0x2994 | ZoneModule 21 - Heating Valve Setpoint % | % | 3x3008 |  | AI3007 |  | 0 | 10000 |  |  | Zone 21; Actual opening, heating valve [1/100 %]
0x2997 | ZoneModule 21 - Cooling Valve Setpoint % | % | 3x3009 |  | AI3008 |  | 0 | 10000 |  |  | Zone 21; Actual opening, cooling valve [1/100 %]
0x2998 | ZoneModule 21 - Room Temperature Actual Value | °C | 3x3010 |  | AI3009 |  | -4000 | 10000 |  |  | Zone 21; Actual room temperature [1/100 °C]
0x299A | ZoneModule 21 - Supply Temperature Actual Value | °C | 3x3011 |  | AI3010 |  | -4000 | 10000 |  |  | Zone 21; Actual inlet temperature [1/100 °C]
0x299B | ZoneModule 21 - Remote Setpoint Offset Actual Value | K | 3x3012 |  | AI3011 |  | -4000 | 10000 |  |  | Zone 21; Actual temperature offset from potentiometer [1/100 °C]
| ZoneModule 21 - CO2/VOC Actual Value | ppm | 3x3013 |  | AI3012 |  | 0 | 5000 |  |  | Zone 21; Actual CO2/VOC level [ppm]
| ZoneModule 21 - RH Actual Value | rh | 3x3014 |  | AI3013 |  | 0 | 10000 |  |  | Zone 21; Actual relative humidity level [%rh]
| ZoneModule 21 - Room Temperature Actual Setpoint | °C | 3x3015 |  | AI3014 |  | -4000 | 10000 |  |  | Zone 21; Actual controller setpoint, room temperature [1/100 °C]
| ZoneModule 21 - Room Panel Air Mode |  | 3x3016 | 3.30 | AI3015 | 3.30 | 0 | 3 |  |  | Zone 21; RPT-20 Room Panel; Actual Air Mode: 0 = Auto 1 = Low 2 = High 3 = Stop
| ZoneModule 21 - Heating Valve Actual Flow | l/h | 3x3017 | 3.30 | AI3016 | 3.30 | 0 | 65535 |  |  | Zone 21; Actual Flow; Heating Valve [l/h]
| ZoneModule 21 - Cooling Valve Actual Flow | l/h | 3x3018 | 3.30 | AI3017 | 3.30 | 0 | 65535 |  |  | Zone 21; Actual Flow; Cooling Valve [l/h]
| ZoneModule 21 - VAV Supply 1 Actual Damper pos. % | % | 3x3019 | 3.30 | AI3018 | 3.30 | 0 | 10000 |  |  | Zone 21; Actual setpoint; VAV Supply 1 damper no. 1 [1/100 %]
| ZoneModule 21 - VAV Supply 2 Actual Damper pos. % | % | 3x3020 | 3.30 | AI3019 | 3.30 | 0 | 10000 |  |  | Zone 21; Actual air quantity;VAV Supply 1 damper no. 1 [m3/h]
| ZoneModule 21 - VAV Extract Actual Damper pos. % | % | 3x3021 | 3.30 | AI3020 | 3.30 | 0 | 10000 |  |  | Zone 21; Actual position; VAV Extract 1 damper no. 1 [1/100 %]
| ZoneModule 21 - EL Heater 1 Temp. Sensor Value | °C | 3x3022 | 3.40 | AI3021 | 3.40 | -4000 | 10000 |  |  | Zone 21; Electric heating Coil 1; Sensor Temperature [1/100 °C]
| ZoneModule 21 - EL Heater 2 Temp. Sensor Value | °C | 3x3023 | 3.40 | AI3022 | 3.40 | -4000 | 10000 |  |  | Zone 21; Electric heating Coil 2; Sensor Temperature [1/100 °C]
| ZoneModule 21 - Ext Aout1 Output | % | 3x3024 | 3.40 | AI3023 | 3.40 | 0 | 10000 |  |  | Zone 21; Extension Module; Actual value Analog Output Aout1 [1/100 V]
| ZoneModule 21 - Ext Aout2 Output | % | 3x3025 | 3.40 | AI3024 | 3.40 | 0 | 10000 |  |  | Zone 21; Extension Module; Actual value Analog Output Aout2 [1/100 V]
| ZoneModule 21 - ZoneModule Alarm Bitmap 1 |  | 3x3026 | 3.40 | AI3025 | 3.40 | 0 | 65535 |  |  | Zone 21; Alarm Bit Map 1 - see tab below: Bit Map Alarm Overview
| ZoneModule 21 - ZoneModule Alarm Bitmap 2 |  | 3x3027 | 3.40 | AI3026 | 3.40 | 0 | 65535 |  |  | Zone 21; Alarm Bit Map 2 - see tab below: Bit Map Alarm Overview
| ZoneModule 21 - ZoneModule Alarm Bitmap 3 |  | 3x3028 | 3.40 | AI3027 | 3.40 | 0 | 65535 |  |  | Zone 21; Alarm Bit Map 3 - see tab below: Bit Map Alarm Overview
| ZoneModule 21 - ZoneModule Alarm Bitmap 4 |  | 3x3029 | 3.40 | AI3028 | 3.40 | 0 | 65535 |  |  | Zone 21; Alarm Bit Map 4 - see tab below: Bit Map Alarm Overview
| ZoneModule 21 - VAV Extract 2 Actuator Setpoint % | % | 3x3030 | 3.40 | AI3029 | 3.40 | 0 | 10000 |  |  | Zone 21; Actual setpoint; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 21 - VAV Extract 2 Actual Flow | m3/h | 3x3031 | 3.40 | AI3030 | 3.40 | 0 | 65535 |  |  | Zone 21; Actual air quantity;VAV Extract 2 damper no. 1 [m3/h]
| ZoneModule 21 - VAV Extract 2 Actual Damper pos. % | % | 3x3032 | 3.40 | AI3031 | 3.40 | 0 | 10000 |  |  | Zone 21; Actual position; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 22 - Status |  | 3x3101 |  | AI3100 |  | 0 | 2 |  |  | Actual status, Zone 22: 0 = Normal 1 = B-alarm 2 = A-alarm
| ZoneModule 22 - VAV Supply 1 Actuator Setpoint % | % | 3x3102 |  | AI3101 |  | 0 | 10000 |  |  | Zone 22; Actual setpoint; VAV inlet damper no. 1 [1/100 %]
| ZoneModule 22 - VAV Supply 1 Actual Flow | m3/h | 3x3103 |  | AI3102 |  | 0 | 65535 |  |  | Zone 22; Actual air quantity; VAV inlet damper no. 1 [m3/h]
| ZoneModule 22 - VAV Supply 2 Actuator Setpoint % | % | 3x3104 |  | AI3103 |  | 0 | 10000 |  |  | Zone 22; Actual setpoint; VAV inlet damper no. 2 [1/100 %]
| ZoneModule 22 - VAV Supply 2 Actual Flow | m3/h | 3x3105 |  | AI3104 |  | 0 | 65535 |  |  | Zone 22; Actual air quantity; VAV inlet damper no. 2 [m3/h]
| ZoneModule 22 - VAV Extract Actuator Setpoint % | % | 3x3106 |  | AI3105 |  | 0 | 10000 |  |  | Zone 22; Actual setpoint; VAV exhaust damper [1/100 %]
| ZoneModule 22 - VAV Extract Actual Flow | m3/h | 3x3107 |  | AI3106 |  | 0 | 65535 |  |  | Zone 22; Actual air quantity; VAV exhaust damper [m3/h]
| ZoneModule 22 - Heating Valve Setpoint % | % | 3x3108 |  | AI3107 |  | 0 | 10000 |  |  | Zone 22; Actual opening, heating valve [1/100 %]
| ZoneModule 22 - Cooling Valve Setpoint % | % | 3x3109 |  | AI3108 |  | 0 | 10000 |  |  | Zone 22; Actual opening, cooling valve [1/100 %]
| ZoneModule 22 - Room Temperature Actual Value | °C | 3x3110 |  | AI3109 |  | -4000 | 10000 |  |  | Zone 22; Actual room temperature [1/100 °C]
| ZoneModule 22 - Supply Temperature Actual Value | °C | 3x3111 |  | AI3110 |  | -4000 | 10000 |  |  | Zone 22; Actual inlet temperature [1/100 °C]
| ZoneModule 22 - Remote Setpoint Offset Actual Value | K | 3x3112 |  | AI3111 |  | -4000 | 10000 |  |  | Zone 22; Actual temperature offset from potentiometer [1/100 °C]
| ZoneModule 22 - CO2/VOC Actual Value | ppm | 3x3113 |  | AI3112 |  | 0 | 5000 |  |  | Zone 22; Actual CO2/VOC level [ppm]
| ZoneModule 22 - RH Actual Value | rh | 3x3114 |  | AI3113 |  | 0 | 10000 |  |  | Zone 22; Actual relative humidity level [%rh]
| ZoneModule 22 - Room Temperature Actual Setpoint | °C | 3x3115 |  | AI3114 |  | -4000 | 10000 |  |  | Zone 22; Actual controller setpoint, room temperature [1/100 °C]
| ZoneModule 22 - Room Panel Air Mode |  | 3x3116 | 3.30 | AI3115 | 3.30 | 0 | 3 |  |  | Zone 22; RPT-20 Room Panel; Actual Air Mode: 0 = Auto 1 = Low 2 = High 3 = Stop
| ZoneModule 22 - Heating Valve Actual Flow | l/h | 3x3117 | 3.30 | AI3116 | 3.30 | 0 | 65535 |  |  | Zone 22; Actual Flow; Heating Valve [l/h]
| ZoneModule 22 - Cooling Valve Actual Flow | l/h | 3x3118 | 3.30 | AI3117 | 3.30 | 0 | 65535 |  |  | Zone 22; Actual Flow; Cooling Valve [l/h]
| ZoneModule 22 - VAV Supply 1 Actual Damper pos. % | % | 3x3119 | 3.30 | AI3118 | 3.30 | 0 | 10000 |  |  | Zone 22; Actual setpoint; VAV Supply 1 damper no. 1 [1/100 %]
| ZoneModule 22 - VAV Supply 2 Actual Damper pos. % | % | 3x3120 | 3.30 | AI3119 | 3.30 | 0 | 10000 |  |  | Zone 22; Actual air quantity;VAV Supply 1 damper no. 1 [m3/h]
| ZoneModule 22 - VAV Extract Actual Damper pos. % | % | 3x3121 | 3.30 | AI3120 | 3.30 | 0 | 10000 |  |  | Zone 22; Actual position; VAV Extract 1 damper no. 1 [1/100 %]
| ZoneModule 22 - EL Heater 1 Temp. Sensor Value | °C | 3x3122 | 3.40 | AI3121 | 3.40 | -4000 | 10000 |  |  | Zone 22; Electric heating Coil 1; Sensor Temperature [1/100 °C]
| ZoneModule 22 - EL Heater 2 Temp. Sensor Value | °C | 3x3123 | 3.40 | AI3122 | 3.40 | -4000 | 10000 |  |  | Zone 22; Electric heating Coil 2; Sensor Temperature [1/100 °C]
| ZoneModule 22 - Ext Aout1 Output | % | 3x3124 | 3.40 | AI3123 | 3.40 | 0 | 10000 |  |  | Zone 22; Extension Module; Actual value Analog Output Aout1 [1/100 V]
| ZoneModule 22 - Ext Aout2 Output | % | 3x3125 | 3.40 | AI3124 | 3.40 | 0 | 10000 |  |  | Zone 22; Extension Module; Actual value Analog Output Aout2 [1/100 V]
| ZoneModule 22 - ZoneModule Alarm Bitmap 1 |  | 3x3126 | 3.40 | AI3125 | 3.40 | 0 | 65535 |  |  | Zone 22; Alarm Bit Map 1 - see tab below: Bit Map Alarm Overview
| ZoneModule 22 - ZoneModule Alarm Bitmap 2 |  | 3x3127 | 3.40 | AI3126 | 3.40 | 0 | 65535 |  |  | Zone 22; Alarm Bit Map 2 - see tab below: Bit Map Alarm Overview
| ZoneModule 22 - ZoneModule Alarm Bitmap 3 |  | 3x3128 | 3.40 | AI3127 | 3.40 | 0 | 65535 |  |  | Zone 22; Alarm Bit Map 3 - see tab below: Bit Map Alarm Overview
| ZoneModule 22 - ZoneModule Alarm Bitmap 4 |  | 3x3129 | 3.40 | AI3128 | 3.40 | 0 | 65535 |  |  | Zone 22; Alarm Bit Map 4 - see tab below: Bit Map Alarm Overview
| ZoneModule 22 - VAV Extract 2 Actuator Setpoint % | % | 3x3130 | 3.40 | AI3129 | 3.40 | 0 | 10000 |  |  | Zone 22; Actual setpoint; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 22 - VAV Extract 2 Actual Flow | m3/h | 3x3131 | 3.40 | AI3130 | 3.40 | 0 | 65535 |  |  | Zone 22; Actual air quantity;VAV Extract 2 damper no. 1 [m3/h]
| ZoneModule 22 - VAV Extract 2 Actual Damper pos. % | % | 3x3132 | 3.40 | AI3131 | 3.40 | 0 | 10000 |  |  | Zone 22; Actual position; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 23 - Status |  | 3x3201 |  | AI3200 |  | 0 | 2 |  |  | Actual status, Zone 23: 0 = Normal 1 = B-alarm 2 = A-alarm
| ZoneModule 23 - VAV Supply 1 Actuator Setpoint % | % | 3x3202 |  | AI3201 |  | 0 | 10000 |  |  | Zone 23; Actual setpoint; VAV inlet damper no. 1 [1/100 %]
| ZoneModule 23 - VAV Supply 1 Actual Flow | m3/h | 3x3203 |  | AI3202 |  | 0 | 65535 |  |  | Zone 23; Actual air quantity; VAV inlet damper no. 1 [m3/h]
| ZoneModule 23 - VAV Supply 2 Actuator Setpoint % | % | 3x3204 |  | AI3203 |  | 0 | 10000 |  |  | Zone 23; Actual setpoint; VAV inlet damper no. 2 [1/100 %]
| ZoneModule 23 - VAV Supply 2 Actual Flow | m3/h | 3x3205 |  | AI3204 |  | 0 | 65535 |  |  | Zone 23; Actual air quantity; VAV inlet damper no. 2 [m3/h]
| ZoneModule 23 - VAV Extract Actuator Setpoint % | % | 3x3206 |  | AI3205 |  | 0 | 10000 |  |  | Zone 23; Actual setpoint; VAV exhaust damper [1/100 %]
| ZoneModule 23 - VAV Extract Actual Flow | m3/h | 3x3207 |  | AI3206 |  | 0 | 65535 |  |  | Zone 23; Actual air quantity; VAV exhaust damper [m3/h]
| ZoneModule 23 - Heating Valve Setpoint % | % | 3x3208 |  | AI3207 |  | 0 | 10000 |  |  | Zone 23; Actual opening, heating valve [1/100 %]
| ZoneModule 23 - Cooling Valve Setpoint % | % | 3x3209 |  | AI3208 |  | 0 | 10000 |  |  | Zone 23; Actual opening, cooling valve [1/100 %]
| ZoneModule 23 - Room Temperature Actual Value | °C | 3x3210 |  | AI3209 |  | -4000 | 10000 |  |  | Zone 23; Actual room temperature [1/100 °C]
| ZoneModule 23 - Supply Temperature Actual Value | °C | 3x3211 |  | AI3210 |  | -4000 | 10000 |  |  | Zone 23; Actual inlet temperature [1/100 °C]
| ZoneModule 23 - Remote Setpoint Offset Actual Value | K | 3x3212 |  | AI3211 |  | -4000 | 10000 |  |  | Zone 23; Actual temperature offset from potentiometer [1/100 °C]
| ZoneModule 23 - CO2/VOC Actual Value | ppm | 3x3213 |  | AI3212 |  | 0 | 5000 |  |  | Zone 23; Actual CO2/VOC level [ppm]
| ZoneModule 23 - RH Actual Value | rh | 3x3214 |  | AI3213 |  | 0 | 10000 |  |  | Zone 23; Actual relative humidity level [%rh]
| ZoneModule 23 - Room Temperature Actual Setpoint | °C | 3x3215 |  | AI3214 |  | -4000 | 10000 |  |  | Zone 23; Actual controller setpoint, room temperature [1/100 °C]
| ZoneModule 23 - Room Panel Air Mode |  | 3x3216 | 3.30 | AI3215 | 3.30 | 0 | 3 |  |  | Zone 23; RPT-20 Room Panel; Actual Air Mode: 0 = Auto 1 = Low 2 = High 3 = Stop
| ZoneModule 23 - Heating Valve Actual Flow | l/h | 3x3217 | 3.30 | AI3216 | 3.30 | 0 | 65535 |  |  | Zone 23; Actual Flow; Heating Valve [l/h]
| ZoneModule 23 - Cooling Valve Actual Flow | l/h | 3x3218 | 3.30 | AI3217 | 3.30 | 0 | 65535 |  |  | Zone 23; Actual Flow; Cooling Valve [l/h]
| ZoneModule 23 - VAV Supply 1 Actual Damper pos. % | % | 3x3219 | 3.30 | AI3218 | 3.30 | 0 | 10000 |  |  | Zone 23; Actual setpoint; VAV Supply 1 damper no. 1 [1/100 %]
| ZoneModule 23 - VAV Supply 2 Actual Damper pos. % | % | 3x3220 | 3.30 | AI3219 | 3.30 | 0 | 10000 |  |  | Zone 23; Actual air quantity;VAV Supply 1 damper no. 1 [m3/h]
| ZoneModule 23 - VAV Extract Actual Damper pos. % | % | 3x3221 | 3.30 | AI3220 | 3.30 | 0 | 10000 |  |  | Zone 23; Actual position; VAV Extract 1 damper no. 1 [1/100 %]
| ZoneModule 23 - EL Heater 1 Temp. Sensor Value | °C | 3x3222 | 3.40 | AI3221 | 3.40 | -4000 | 10000 |  |  | Zone 23; Electric heating Coil 1; Sensor Temperature [1/100 °C]
| ZoneModule 23 - EL Heater 2 Temp. Sensor Value | °C | 3x3223 | 3.40 | AI3222 | 3.40 | -4000 | 10000 |  |  | Zone 23; Electric heating Coil 2; Sensor Temperature [1/100 °C]
| ZoneModule 23 - Ext Aout1 Output | % | 3x3224 | 3.40 | AI3223 | 3.40 | 0 | 10000 |  |  | Zone 23; Extension Module; Actual value Analog Output Aout1 [1/100 V]
| ZoneModule 23 - Ext Aout2 Output | % | 3x3225 | 3.40 | AI3224 | 3.40 | 0 | 10000 |  |  | Zone 23; Extension Module; Actual value Analog Output Aout2 [1/100 V]
| ZoneModule 23 - ZoneModule Alarm Bitmap 1 |  | 3x3226 | 3.40 | AI3225 | 3.40 | 0 | 65535 |  |  | Zone 23; Alarm Bit Map 1 - see tab below: Bit Map Alarm Overview
| ZoneModule 23 - ZoneModule Alarm Bitmap 2 |  | 3x3227 | 3.40 | AI3226 | 3.40 | 0 | 65535 |  |  | Zone 23; Alarm Bit Map 2 - see tab below: Bit Map Alarm Overview
| ZoneModule 23 - ZoneModule Alarm Bitmap 3 |  | 3x3228 | 3.40 | AI3227 | 3.40 | 0 | 65535 |  |  | Zone 23; Alarm Bit Map 3 - see tab below: Bit Map Alarm Overview
| ZoneModule 23 - ZoneModule Alarm Bitmap 4 |  | 3x3229 | 3.40 | AI3228 | 3.40 | 0 | 65535 |  |  | Zone 23; Alarm Bit Map 4 - see tab below: Bit Map Alarm Overview
| ZoneModule 23 - VAV Extract 2 Actuator Setpoint % | % | 3x3230 | 3.40 | AI3229 | 3.40 | 0 | 10000 |  |  | Zone 23; Actual setpoint; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 23 - VAV Extract 2 Actual Flow | m3/h | 3x3231 | 3.40 | AI3230 | 3.40 | 0 | 65535 |  |  | Zone 23; Actual air quantity;VAV Extract 2 damper no. 1 [m3/h]
| ZoneModule 23 - VAV Extract 2 Actual Damper pos. % | % | 3x3232 | 3.40 | AI3231 | 3.40 | 0 | 10000 |  |  | Zone 23; Actual position; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 24 - Status |  | 3x3301 |  | AI3300 |  | 0 | 2 |  |  | Actual status, Zone 24: 0 = Normal 1 = B-alarm 2 = A-alarm
| ZoneModule 24 - VAV Supply 1 Actuator Setpoint % | % | 3x3302 |  | AI3301 |  | 0 | 10000 |  |  | Zone 24; Actual setpoint; VAV inlet damper no. 1 [1/100 %]
| ZoneModule 24 - VAV Supply 1 Actual Flow | m3/h | 3x3303 |  | AI3302 |  | 0 | 65535 |  |  | Zone 24; Actual air quantity; VAV inlet damper no. 1 [m3/h]
| ZoneModule 24 - VAV Supply 2 Actuator Setpoint % | % | 3x3304 |  | AI3303 |  | 0 | 10000 |  |  | Zone 24; Actual setpoint; VAV inlet damper no. 2 [1/100 %]
| ZoneModule 24 - VAV Supply 2 Actual Flow | m3/h | 3x3305 |  | AI3304 |  | 0 | 65535 |  |  | Zone 24; Actual air quantity; VAV inlet damper no. 2 [m3/h]
| ZoneModule 24 - VAV Extract Actuator Setpoint % | % | 3x3306 |  | AI3305 |  | 0 | 10000 |  |  | Zone 24; Actual setpoint; VAV exhaust damper [1/100 %]
| ZoneModule 24 - VAV Extract Actual Flow | m3/h | 3x3307 |  | AI3306 |  | 0 | 65535 |  |  | Zone 24; Actual air quantity; VAV exhaust damper [m3/h]
| ZoneModule 24 - Heating Valve Setpoint % | % | 3x3308 |  | AI3307 |  | 0 | 10000 |  |  | Zone 24; Actual opening, heating valve [1/100 %]
| ZoneModule 24 - Cooling Valve Setpoint % | % | 3x3309 |  | AI3308 |  | 0 | 10000 |  |  | Zone 24; Actual opening, cooling valve [1/100 %]
| ZoneModule 24 - Room Temperature Actual Value | °C | 3x3310 |  | AI3309 |  | -4000 | 10000 |  |  | Zone 24; Actual room temperature [1/100 °C]
| ZoneModule 24 - Supply Temperature Actual Value | °C | 3x3311 |  | AI3310 |  | -4000 | 10000 |  |  | Zone 24; Actual inlet temperature [1/100 °C]
| ZoneModule 24 - Remote Setpoint Offset Actual Value | K | 3x3312 |  | AI3311 |  | -4000 | 10000 |  |  | Zone 24; Actual temperature offset from potentiometer [1/100 °C]
| ZoneModule 24 - CO2/VOC Actual Value | ppm | 3x3313 |  | AI3312 |  | 0 | 5000 |  |  | Zone 24; Actual CO2/VOC level [ppm]
| ZoneModule 24 - RH Actual Value | rh | 3x3314 |  | AI3313 |  | 0 | 10000 |  |  | Zone 24; Actual relative humidity level [%rh]
| ZoneModule 24 - Room Temperature Actual Setpoint | °C | 3x3315 |  | AI3314 |  | -4000 | 10000 |  |  | Zone 24; Actual controller setpoint, room temperature [1/100 °C]
| ZoneModule 24 - Room Panel Air Mode |  | 3x3316 | 3.30 | AI3315 | 3.30 | 0 | 3 |  |  | Zone 24; RPT-20 Room Panel; Actual Air Mode: 0 = Auto 1 = Low 2 = High 3 = Stop
| ZoneModule 24 - Heating Valve Actual Flow | l/h | 3x3317 | 3.30 | AI3316 | 3.30 | 0 | 65535 |  |  | Zone 24; Actual Flow; Heating Valve [l/h]
| ZoneModule 24 - Cooling Valve Actual Flow | l/h | 3x3318 | 3.30 | AI3317 | 3.30 | 0 | 65535 |  |  | Zone 24; Actual Flow; Cooling Valve [l/h]
| ZoneModule 24 - VAV Supply 1 Actual Damper pos. % | % | 3x3319 | 3.30 | AI3318 | 3.30 | 0 | 10000 |  |  | Zone 24; Actual setpoint; VAV Supply 1 damper no. 1 [1/100 %]
| ZoneModule 24 - VAV Supply 2 Actual Damper pos. % | % | 3x3320 | 3.30 | AI3319 | 3.30 | 0 | 10000 |  |  | Zone 24; Actual air quantity;VAV Supply 1 damper no. 1 [m3/h]
| ZoneModule 24 - VAV Extract Actual Damper pos. % | % | 3x3321 | 3.30 | AI3320 | 3.30 | 0 | 10000 |  |  | Zone 24; Actual position; VAV Extract 1 damper no. 1 [1/100 %]
| ZoneModule 24 - EL Heater 1 Temp. Sensor Value | °C | 3x3322 | 3.40 | AI3321 | 3.40 | -4000 | 10000 |  |  | Zone 24; Electric heating Coil 1; Sensor Temperature [1/100 °C]
| ZoneModule 24 - EL Heater 2 Temp. Sensor Value | °C | 3x3323 | 3.40 | AI3322 | 3.40 | -4000 | 10000 |  |  | Zone 24; Electric heating Coil 2; Sensor Temperature [1/100 °C]
| ZoneModule 24 - Ext Aout1 Output | % | 3x3324 | 3.40 | AI3323 | 3.40 | 0 | 10000 |  |  | Zone 24; Extension Module; Actual value Analog Output Aout1 [1/100 V]
| ZoneModule 24 - Ext Aout2 Output | % | 3x3325 | 3.40 | AI3324 | 3.40 | 0 | 10000 |  |  | Zone 24; Extension Module; Actual value Analog Output Aout2 [1/100 V]
| ZoneModule 24 - ZoneModule Alarm Bitmap 1 |  | 3x3326 | 3.40 | AI3325 | 3.40 | 0 | 65535 |  |  | Zone 24; Alarm Bit Map 1 - see tab below: Bit Map Alarm Overview
| ZoneModule 24 - ZoneModule Alarm Bitmap 2 |  | 3x3327 | 3.40 | AI3326 | 3.40 | 0 | 65535 |  |  | Zone 24; Alarm Bit Map 2 - see tab below: Bit Map Alarm Overview
| ZoneModule 24 - ZoneModule Alarm Bitmap 3 |  | 3x3328 | 3.40 | AI3327 | 3.40 | 0 | 65535 |  |  | Zone 24; Alarm Bit Map 3 - see tab below: Bit Map Alarm Overview
| ZoneModule 24 - ZoneModule Alarm Bitmap 4 |  | 3x3329 | 3.40 | AI3328 | 3.40 | 0 | 65535 |  |  | Zone 24; Alarm Bit Map 4 - see tab below: Bit Map Alarm Overview
| ZoneModule 24 - VAV Extract 2 Actuator Setpoint % | % | 3x3330 | 3.40 | AI3329 | 3.40 | 0 | 10000 |  |  | Zone 24; Actual setpoint; VAV Extract 2 damper no. 1 [1/100 %]
| ZoneModule 24 - VAV Extract 2 Actual Flow | m3/h | 3x3331 | 3.40 | AI3330 | 3.40 | 0 | 65535 |  |  | Zone 24; Actual air quantity;VAV Extract 2 damper no. 1 [m3/h]
| ZoneModule 24 - VAV Extract 2 Actual Damper pos. % | % | 3x3332 | 3.40 | AI3331 | 3.40 | 0 | 10000 |  |  | Zone 24; Actual position; VAV Extract 2 damper no. 1 [1/100 %]
0x299C | ZoneModule 25 - Status |  | 3x3401 |  | AI3400 |  | 0 | 2 |  |  | Actual status, Zone 25: 0 = Normal 1 = B-alarm 2 = A-alarm
0x2960 | ZoneModule 25 - VAV Supply 1 Actuator Setpoint % | % | 3x3402 |  | AI3401 |  | 0 | 10000 |  |  | Zone 25; Actual setpoint; VAV inlet damper no. 1 [1/100 %]
0x2961 | ZoneModule 25 - VAV Supply 1 Actual Flow | m3/h | 3x3403 |  | AI3402 |  | 0 | 65535 |  |  | Zone 25; Actual air quantity; VAV inlet damper no. 1 [m3/h]
0x2962 | ZoneModule 25 - VAV Supply 2 Actuator Setpoint % | % | 3x3404 |  | AI3403 |  | 0 | 10000 |  |  | Zone 25; Actual setpoint; VAV inlet damper no. 2 [1/100 %]
0x2963 | ZoneModule 25 - VAV Supply 2 Actual Flow | m3/h | 3x3405 |  | AI3404 |  | 0 | 65535 |  |  | Zone 25; Actual air quantity; VAV inlet damper no. 2 [m3/h]
0x2964 | ZoneModule 25 - VAV Extract Actuator Setpoint % | % | 3x3406 |  | AI3405 |  | 0 | 10000 |  |  | Zone 25; Actual setpoint; VAV exhaust damper [1/100 %]
0x2967 | ZoneModule 25 - VAV Extract Actual Flow | m3/h | 3x3407 |  | AI3406 |  | 0 | 65535 |  |  | Zone 25; Actual air quantity; VAV exhaust damper [m3/h]
0x2968 | ZoneModule 25 - Heating Valve Setpoint % | % | 3x3408 |  | AI3407 |  | 0 | 10000 |  |  | Zone 25; Actual opening, heating valve [1/100 %]
0x296A | ZoneModule 25 - Cooling Valve Setpoint % | % | 3x3409 |  | AI3408 |  | 0 | 10000 |  |  | Zone 25; Actual opening, cooling valve [1/100 %]
0x296B | ZoneModule 25 - Room Temperature Actual Value | °C | 3x3410 |  | AI3409 |  | -4000 | 10000 |  |  | Zone 25; Actual room temperature [1/100 °C]
0x296C | ZoneModule 25 - Supply Temperature Actual Value | °C | 3x3411 |  | AI3410 |  | -4000 | 10000 |  |  | Zone 25; Actual inlet temperature [1/100 °C]
0x2972 | ZoneModule 25 - Remote Setpoint Offset Actual Value | K | 3x3412 |  | AI3411 |  | -4000 | 10000 |  |  | Zone 25; Actual temperature offset from potentiometer [1/100 °C]
0x2973 | ZoneModule 25 - CO2/VOC Actual Value | ppm | 3x3413 |  | AI3412 |  | 0 | 5000 |  |  | Zone 25; Actual CO2/VOC level [ppm]
0x2974 | ZoneModule 25 - RH Actual Value | rh | 3x3414 |  | AI3413 |  | 0 | 10000 |  |  | Zone 25; Actual relative humidity level [%rh]
0x2977 | ZoneModule 25 - Room Temperature Actual Setpoint | °C | 3x3415 |  | AI3414 |  | -4000 | 10000 |  |  | Zone 25; Actual controller setpoint, room temperature [1/100 °C]
0x2978 | ZoneModule 25 - Room Panel Air Mode |  | 3x3416 | 3.30 | AI3415 | 3.30 | 0 | 3 |  |  | Zone 25; RPT-20 Room Panel; Actual Air Mode: 0 = Auto 1 = Low 2 = High 3 = Stop
0x297A | ZoneModule 25 - Heating Valve Actual Flow | l/h | 3x3417 | 3.30 | AI3416 | 3.30 | 0 | 65535 |  |  | Zone 25; Actual Flow; Heating Valve [l/h]
0x297B | ZoneModule 25 - Cooling Valve Actual Flow | l/h | 3x3418 | 3.30 | AI3417 | 3.30 | 0 | 65535 |  |  | Zone 25; Actual Flow; Cooling Valve [l/h]
0x297C | ZoneModule 25 - VAV Supply 1 Actual Damper pos. % | % | 3x3419 | 3.30 | AI3418 | 3.30 | 0 | 10000 |  |  | Zone 25; Actual setpoint; VAV Supply 1 damper no. 1 [1/100 %]
0x2970 | ZoneModule 25 - VAV Supply 2 Actual Damper pos. % | % | 3x3420 | 3.30 | AI3419 | 3.30 | 0 | 10000 |  |  | Zone 25; Actual air quantity;VAV Supply 1 damper no. 1 [m3/h]
0x2971 | ZoneModule 25 - VAV Extract Actual Damper pos. % | % | 3x3421 | 3.30 | AI3420 | 3.30 | 0 | 10000 |  |  | Zone 25; Actual position; VAV Extract 1 damper no. 1 [1/100 %]
0x2104 | ZoneModule 25 - EL Heater 1 Temp. Sensor Value | °C | 3x3422 | 3.40 | AI3421 | 3.40 | -4000 | 10000 |  |  | Zone 25; Electric heating Coil 1; Sensor Temperature [1/100 °C]
0x2304 | ZoneModule 25 - EL Heater 2 Temp. Sensor Value | °C | 3x3423 | 3.40 | AI3422 | 3.40 | -4000 | 10000 |  |  | Zone 25; Electric heating Coil 2; Sensor Temperature [1/100 °C]
0x2410 | ZoneModule 25 - Ext Aout1 Output | % | 3x3424 | 3.40 | AI3423 | 3.40 | 0 | 10000 |  |  | Zone 25; Extension Module; Actual value Analog Output Aout1 [1/100 V]
0x2352 | ZoneModule 25 - Ext Aout2 Output | % | 3x3425 | 3.40 | AI3424 | 3.40 | 0 | 10000 |  |  | Zone 25; Extension Module; Actual value Analog Output Aout2 [1/100 V]
0x23D0 | ZoneModule 25 - ZoneModule Alarm Bitmap 1 |  | 3x3426 | 3.40 | AI3425 | 3.40 | 0 | 65535 |  |  | Zone 25; Alarm Bit Map 1 - see tab below: Bit Map Alarm Overview
0x23D1 | ZoneModule 25 - ZoneModule Alarm Bitmap 2 |  | 3x3427 | 3.40 | AI3426 | 3.40 | 0 | 65535 |  |  | Zone 25; Alarm Bit Map 2 - see tab below: Bit Map Alarm Overview
0x242C | ZoneModule 25 - ZoneModule Alarm Bitmap 3 |  | 3x3428 | 3.40 | AI3427 | 3.40 | 0 | 65535 |  |  | Zone 25; Alarm Bit Map 3 - see tab below: Bit Map Alarm Overview
0x2AF9 | ZoneModule 25 - ZoneModule Alarm Bitmap 4 |  | 3x3429 | 3.40 | AI3428 | 3.40 | 0 | 65535 |  |  | Zone 25; Alarm Bit Map 4 - see tab below: Bit Map Alarm Overview
0x2AF1 | ZoneModule 25 - VAV Extract 2 Actuator Setpoint % | % | 3x3430 | 3.40 | AI3429 | 3.40 | 0 | 10000 |  |  | Zone 25; Actual setpoint; VAV Extract 2 damper no. 1 [1/100 %]
0x2107 | ZoneModule 25 - VAV Extract 2 Actual Flow | m3/h | 3x3431 | 3.40 | AI3430 | 3.40 | 0 | 65535 |  |  | Zone 25; Actual air quantity;VAV Extract 2 damper no. 1 [m3/h]
0x2227 | ZoneModule 25 - VAV Extract 2 Actual Damper pos. % | % | 3x3432 | 3.40 | AI3431 | 3.40 | 0 | 10000 |  |  | Zone 25; Actual position; VAV Extract 2 damper no. 1 [1/100 %]
0x23A7 | Number Of Zonemasters |  | 3x3501 |  | AI3500 |  | 0 | 5 |  |  | Actual number of interconnected zone masters
0x248C | ZoneMaster Chain ID |  | 3x3502 |  | AI3501 |  | 0 | 4 |  |  | ID of this zone master
0x210A | ZoneMaster 1 - ZoneMaster Local Alarm Status |  | 3x4001 |  | AI4000 |  | 0 | 2 |  |  | Alarm status for zone master no. 1 [0=Normal; 1=B-alarm; 2=A-alarm]
0x222A | ZoneMaster 2 - ZoneMaster Local Alarm Status |  | 3x4101 |  | AI4100 |  | 0 | 2 |  |  | Alarm status for zone master no. 2 [0=Normal; 1=B-alarm; 2=A-alarm]
| ZoneMaster 3 - ZoneMaster Local Alarm Status |  | 3x4201 |  | AI4200 |  | 0 | 2 |  |  | Alarm status for zone master no. 3 [0=Normal; 1=B-alarm; 2=A-alarm]
| ZoneMaster 4 - ZoneMaster Local Alarm Status |  | 3x4301 |  | AI4300 |  | 0 | 2 |  |  | Alarm status for zone master no. 4 [0=Normal; 1=B-alarm; 2=A-alarm]
| ZoneMaster 5 - ZoneMaster Local Alarm Status |  | 3x4401 |  | AI4400 |  | 0 | 2 |  |  | Alarm status for zone master no. 5 [0=Normal; 1=B-alarm; 2=A-alarm]
| 1. Info |  | Holding register (R/W) |  | Analog value (R/W) | 1. Info | 1. Info | 1. Info |  |  | 1. Info
0x3000 | System Time Year |  | 4x0001 |  | AV0 |  | 2000 | 2200 |  |  | Actual year in zone master
0x3440 | System Time Month |  | 4x0002 |  | AV1 |  | 1 | 12 |  |  | Actual month in zone master
0x3161 | System Time Date |  | 4x0003 |  | AV2 |  | 1 | 31 |  |  | Actual date in zone master
0x3162 | System Time Hour |  | 4x0004 |  | AV3 |  | 0 | 23 |  |  | Actual time in zone master
0x3163 | System Time Minute |  | 4x0005 |  | AV4 |  | 0 | 59 |  |  | Actual minute in zone master
0x3164 | System Time Second |  | 4x0006 |  | AV5 |  | 0 | 59 |  |  | Actual second in zone master
0x3261 | AHU Min Supply Fan Speed | % | 4x0101 |  | AV100 |  | 0 | 10000 |  |  | Inlet fan, min. speed [1/100 %]
0x3262 | AHU Max Supply Fan Speed | % | 4x0102 |  | AV101 |  | 0 | 10000 |  |  | Inlet fan, max. speed [1/100 %]
0x3263 | AHU Min Extract Fan Speed | % | 4x0103 |  | AV102 |  | 0 | 10000 |  |  | Exhaust fan, min. speed [1/100 %]
0x3264 | AHU Max Extract Fan Speed | % | 4x0104 |  | AV103 |  | 0 | 10000 |  |  | Exhaust fan, max. speed [1/100 %]
0x3120 | Minimum Supply Air Temperature | °C | 4x0105 |  | AV104 |  | 0 | 3000 |  |  | Min. inlet temperature [1/100 °C]
0x3121 | Highest Allowed Cooling Water Temp | °C | 4x0106 |  | AV105 |  | -4000 | 10000 |  |  | Alarm limit for max. cooling water temperature [1/100 °C]
0x3220 | Lowest Allowed Heating Water Temp | °C | 4x0107 |  | AV106 |  | -4000 | 10000 |  |  | Alarm limit for min. heating water temperature [1/100 °C]
0x3221 | Winter Start Temperature | °C | 4x0108 |  | AV107 |  | -1000 | 1000 |  |  | Summer/winter compensation, outdoor temperature for start of winter setting [1/100 °C]
0x3441 | Winter Max Temperature | °C | 4x0109 |  | AV108 |  | -3000 | -1000 |  |  | Summer/winter compensation, outdoor temperature for end of winter setting [1/100 °C]
0x3441 | Winter Temp Diff | °C | 4x0110 |  | AV109 |  | 0 | 1000 |  |  | Summer/winter compensation, winter compensation [1/100 °C]
0x3441 | Summer Start Temperature | °C | 4x0111 |  | AV110 |  | 1000 | 3000 |  |  | Summer/winter compensation, outdoor temperature for start of summer setting [1/100 °C]
0x3450 | Summer Max Temperature | °C | 4x0112 |  | AV111 |  | 2000 | 4000 |  |  | Summer/winter compensation, outdoor temperature for end of summer setting [1/100 °C]
0x3451 | Summer Temp Diff | °C | 4x0113 | 3.30 | AV112 | 3.30 | -1000 | 1000 |  |  | Summer/winter compensation, summer compensation [1/100 °C]
0x3456 | Max Supply Pressure | Pa | 4x0114 | 3.30 | AV113 | 3.30 | 0 | 2500 |  |  | Pressure in supply air duct
0x3457 | Max Extract Pressure | Pa | 4x0115 | 3.30 | AV114 | 3.30 | 0 | 2500 |  |  | Pressure in extract air duct
0x3458 | ZoneModule 1 - Room Temperature Setpoint | °C | 4x1002 |  | AV1001 |  | 1000 | 4500 |  |  | Zone 1 - Setpoint for room temperature [1/100 °C]
0x3453 | ZoneModule 1 - Minimum Supply Temperature | °C | 4x1003 |  | AV1002 |  | 1000 | 3000 |  |  | Zone 1 - Setpoint for min. inlet temperature [1/100 °C]
0x3454 | ZoneModule 1 - Maximum Supply Temperature | °C | 4x1004 |  | AV1003 |  | 1000 | 6000 |  |  | Zone 1 - Max. setpoint inlet temperature [1/100 °C]
0x3455 | ZoneModule 1 - Room CO2 Setpoint | ppm | 4x1005 |  | AV1004 |  | 100 | 5000 |  |  | Zone 1 - Setpoint for CO2 [ppm]
0x3470 | ZoneModule 1 - Room RH Setpoint | % | 4x1006 |  | AV1005 |  | 0 | 10000 |  |  | Zone 1 - Setpoint for relative humidity [1/100 %rh]
0x3471 | ZoneModule 1 - VAV Supply PIR Min. Air Flow | m3/h | 4x1007 |  | AV1006 |  | 0 | 65535 |  |  | Zone 1 - Min. inlet air quantity with PIR active [1/100 %]
0x3472 | ZoneModule 1 - VAV Supply 1 Min. Air Flow | m3/h | 4x1008 |  | AV1007 |  | 0 | 65535 |  |  | Zone 1 - Min. inlet air quantity, VAV damper 1 [1/100 %]
0x3473 | ZoneModule 1 - VAV Supply 1 Max. Air Flow | m3/h | 4x1009 |  | AV1008 |  | 0 | 65535 |  |  | Zone 1 - Max. inlet air quantity, VAV damper 1 [1/100 %]
0x3474 | ZoneModule 1 - VAV Supply 2 Min. Air Flow | m3/h | 4x1010 |  | AV1009 |  | 0 | 65535 |  |  | Zone 1 - Min. inlet air quantity, VAV damper 2 [1/100 %]
0x3143 | ZoneModule 1 - VAV Supply 2 Max. Air Flow | m3/h | 4x1011 |  | AV1010 |  | 0 | 65535 |  |  | Zone 1 - Max. inlet air quantity, VAV damper 2 [1/100 %]
0x3243 | ZoneModule 1 - VAV Extract Min. Air Flow | m3/h | 4x1012 |  | AV1011 |  | 0 | 65535 |  |  | Zone 1 - Min. extract1 air quantity [1/100 %]
0x3122 | ZoneModule 1 - VAV Extract Max. Air Flow | m3/h | 4x1013 |  | AV1012 |  | 0 | 65535 |  |  | Zone 1 - Max. extract1 air quantity [1/100 %]
0x3222 | ZoneModule 1 - VAV Supply 1 Nominal Air Flow | m3/h | 4x1014 | 3.30 | AV1013 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 1 actuator
0x3001 | ZoneModule 1 - VAV Supply 2 Nominal Air Flow | m3/h | 4x1015 | 3.30 | AV1014 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 2 actuator
0x33C0 | ZoneModule 1 - VAV Extract Nominal Air Flow | m3/h | 4x1016 | 3.30 | AV1015 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Extract actuator
0x33C1 | ZoneModule 1 - Room Panel Low Air Flow | % | 4x1017 | 3.30 | AV1016 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “Low”
0x33C2 | ZoneModule 1 - Room Panel High Air Flow | % | 4x1018 | 3.30 | AV1017 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “High”
0x3347 | ZoneModule 1 - Room Panel Override Timeout | min | 4x1019 | 3.30 | AV1018 | 3.30 | 10 | 90 |  |  | Time in minutes after which override from RPT will be reset
0x3348 | ZoneModule 1 - Heat Valve Max. Flow | l/h | 4x1020 | 3.30 | AV1019 | 3.30 | 0 | 65535 |  |  | Maximum flow for Heating Valve (if actuator supports flow measurements)
0x3349 | ZoneModule 1 - Cool Valve Max. Flow | l/h | 4x1021 | 3.30 | AV1020 | 3.30 | 0 | 65535 |  |  | Maximum flow for Cooling Valve (if actuator supports flow measurements)
| ZoneModule 1 - VAV Extract2 Nominal Air Flow | m3/h | 4x1023 | 3.40 | AV1022 | 3.40 | 0 | 65535 |  |  | Zone 1 - Nominal air flow of the Extract2 actuator
| ZoneModule 1 - VAV Extract2 Min. Air Flow | m3/h | 4x1024 | 3.40 | AV1023 | 3.40 | 0 | 65535 |  |  | Zone 1 - Min. Extract2 air quantity [1/100 %]
| ZoneModule 1 - VAV Extract2 Max. Air Flow | m3/h | 4x1025 | 3.40 | AV1024 | 3.40 | 0 | 65535 |  |  | Zone 1 - Max. Extract2 air quantity [1/100 %]
0x3800 | ZoneModule 2 - Room Temperature Setpoint | °C | 4x1102 |  | AV1101 |  | 1000 | 4500 |  |  | Zone 2 - Setpoint for room temperature [1/100 °C]
0x3801 | ZoneModule 2 - Minimum Supply Temperature | °C | 4x1103 |  | AV1102 |  | 1000 | 3000 |  |  | Zone 2 - Setpoint for min. inlet temperature [1/100 °C]
0x3802 | ZoneModule 2 - Maximum Supply Temperature | °C | 4x1104 |  | AV1103 |  | 1000 | 6000 |  |  | Zone 2 - Setpoint for max. inlet temperature [1/100 °C]
0x3803 | ZoneModule 2 - Room CO2 Setpoint | ppm | 4x1105 |  | AV1104 |  | 100 | 5000 |  |  | Zone 2 - Setpoint for CO2 [ppm]
0x3804 | ZoneModule 2 - Room RH Setpoint | % | 4x1106 |  | AV1105 |  | 0 | 10000 |  |  | Zone 2 - Setpoint for relative humidity [1/100 %rh]
0x3805 | ZoneModule 2 - VAV Supply PIR Min. Air Flow | m3/h | 4x1107 |  | AV1106 |  | 0 | 65535 |  |  | Zone 2 - Min. inlet air quantity with PIR active [1/100 %]
0x3808 | ZoneModule 2 - VAV Supply 1 Min. Air Flow | m3/h | 4x1108 |  | AV1107 |  | 0 | 65535 |  |  | Zone 2 - Min. inlet air quantity, VAV damper 1 [1/100 %]
0x3809 | ZoneModule 2 - VAV Supply 1 Max. Air Flow | m3/h | 4x1109 |  | AV1108 |  | 0 | 65535 |  |  | Zone 2 - Max. inlet air quantity, VAV damper 1 [1/100 %]
0x380A | ZoneModule 2 - VAV Supply 2 Min. Air Flow | m3/h | 4x1110 |  | AV1109 |  | 0 | 65535 |  |  | Zone 2 - Min. inlet air quantity, VAV damper 2 [1/100 %]
0x380B | ZoneModule 2 - VAV Supply 2 Max. Air Flow | m3/h | 4x1111 |  | AV1110 |  | 0 | 65535 |  |  | Zone 2 - Max. inlet air quantity, VAV damper 2 [1/100 %]
0x3870 | ZoneModule 2 - VAV Extract Min. Air Flow | m3/h | 4x1112 |  | AV1111 |  | 0 | 65535 |  |  | Zone 2 - Min. exhaust air quantity [1/100 %]
0x3810 | ZoneModule 2 - VAV Extract Max. Air Flow | m3/h | 4x1113 |  | AV1112 |  | 0 | 65535 |  |  | Zone 2 - Max. exhaust air quantity [1/100 %]
0x3811 | ZoneModule 2 - VAV Supply 1 Nominal Air Flow | m3/h | 4x1114 | 3.30 | AV1113 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 1 actuator
0x3812 | ZoneModule 2 - VAV Supply 2 Nominal Air Flow | m3/h | 4x1115 | 3.30 | AV1114 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 2 actuator
0x3813 | ZoneModule 2 - VAV Extract Nominal Air Flow | m3/h | 4x1116 | 3.30 | AV1115 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Extract actuator
0x3814 | ZoneModule 2 - Room Panel Low Air Flow | % | 4x1117 | 3.30 | AV1116 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “Low”
0x3815 | ZoneModule 2 - Room Panel High Air Flow | % | 4x1118 | 3.30 | AV1117 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “High”
0x3816 | ZoneModule 2 - Room Panel Override Timeout | min | 4x1119 | 3.30 | AV1118 | 3.30 | 10 | 90 |  |  | Time in minutes after which override from RPT will be reset
0x3817 | ZoneModule 2 - Heat Valve Max. Flow | l/h | 4x1120 | 3.30 | AV1119 | 3.30 | 0 | 65535 |  |  | Maximum flow for Heating Valve (if actuator supports flow measurements)
0x3818 | ZoneModule 2 - Cool Valve Max. Flow | l/h | 4x1121 | 3.30 | AV1120 | 3.30 | 0 | 65535 |  |  | Maximum flow for Cooling Valve (if actuator supports flow measurements)
| ZoneModule 2 - VAV Extract2 Nominal Air Flow | m3/h | 4x1123 | 3.40 | AV1122 | 3.40 | 0 | 65535 |  |  | Zone 2 - Nominal air flow of the Extract2 actuator
| ZoneModule 2 - VAV Extract2 Min. Air Flow | m3/h | 4x1124 | 3.40 | AV1123 | 3.40 | 0 | 65535 |  |  | Zone 2 - Min. Extract2 air quantity [1/100 %]
| ZoneModule 2 - VAV Extract2 Max. Air Flow | m3/h | 4x1125 | 3.40 | AV1124 | 3.40 | 0 | 65535 |  |  | Zone 2 - Max. Extract2 air quantity [1/100 %]
0x381A | ZoneModule 3 - Room Temperature Setpoint | °C | 4x1202 |  | AV1201 |  | 1000 | 4500 |  |  | Zone 3 - Setpoint for room temperature [1/100 °C]
0x381B | ZoneModule 3 - Minimum Supply Temperature | °C | 4x1203 |  | AV1202 |  | 1000 | 3000 |  |  | Zone 3 - Setpoint for min. inlet temperature [1/100 °C]
0x381C | ZoneModule 3 - Maximum Supply Temperature | °C | 4x1204 |  | AV1203 |  | 1000 | 6000 |  |  | Zone 3 - Setpoint for max. inlet temperature [1/100 °C]
0x381D | ZoneModule 3 - Room CO2 Setpoint | ppm | 4x1205 |  | AV1204 |  | 100 | 5000 |  |  | Zone 3 - Setpoint for CO2 [ppm]
0x381E | ZoneModule 3 - Room RH Setpoint | % | 4x1206 |  | AV1205 |  | 0 | 10000 |  |  | Zone 3 - Setpoint for relative humidity [1/100 %rh]
0x381F | ZoneModule 3 - VAV Supply PIR Min. Air Flow | m3/h | 4x1207 |  | AV1206 |  | 0 | 65535 |  |  | Zone 3 - Min. inlet air quantity with PIR active [1/100 %]
0x3820 | ZoneModule 3 - VAV Supply 1 Min. Air Flow | m3/h | 4x1208 |  | AV1207 |  | 0 | 65535 |  |  | Zone 3 - Min. inlet air quantity, VAV damper 1 [1/100 %]
0x3821 | ZoneModule 3 - VAV Supply 1 Max. Air Flow | m3/h | 4x1209 |  | AV1208 |  | 0 | 65535 |  |  | Zone 3 - Max. inlet air quantity, VAV damper 1 [1/100 %]
0x3822 | ZoneModule 3 - VAV Supply 2 Min. Air Flow | m3/h | 4x1210 |  | AV1209 |  | 0 | 65535 |  |  | Zone 3 - Min. inlet air quantity, VAV damper 2 [1/100 %]
0x3823 | ZoneModule 3 - VAV Supply 2 Max. Air Flow | m3/h | 4x1211 |  | AV1210 |  | 0 | 65535 |  |  | Zone 3 - Max. inlet air quantity, VAV damper 2 [1/100 %]
0x3824 | ZoneModule 3 - VAV Extract Min. Air Flow | m3/h | 4x1212 |  | AV1211 |  | 0 | 65535 |  |  | Zone 3 - Min. exhaust air quantity [1/100 %]
0x3825 | ZoneModule 3 - VAV Extract Max. Air Flow | m3/h | 4x1213 |  | AV1212 |  | 0 | 65535 |  |  | Zone 3 - Max. exhaust air quantity [1/100 %]
0x3826 | ZoneModule 3 - VAV Supply 1 Nominal Air Flow | m3/h | 4x1214 | 3.30 | AV1213 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 1 actuator
0x3827 | ZoneModule 3 - VAV Supply 2 Nominal Air Flow | m3/h | 4x1215 | 3.30 | AV1214 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 2 actuator
0x3828 | ZoneModule 3 - VAV Extract Nominal Air Flow | m3/h | 4x1216 | 3.30 | AV1215 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Extract actuator
0x3829 | ZoneModule 3 - Room Panel Low Air Flow | % | 4x1217 | 3.30 | AV1216 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “Low”
0x382A | ZoneModule 3 - Room Panel High Air Flow | % | 4x1218 | 3.30 | AV1217 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “High”
0x382B | ZoneModule 3 - Room Panel Override Timeout | min | 4x1219 | 3.30 | AV1218 | 3.30 | 10 | 90 |  |  | Time in minutes after which override from RPT will be reset
0x3830 | ZoneModule 3 - Heat Valve Max. Flow | l/h | 4x1220 | 3.30 | AV1219 | 3.30 | 0 | 65535 |  |  | Maximum flow for Heating Valve (if actuator supports flow measurements)
0x3831 | ZoneModule 3 - Cool Valve Max. Flow | l/h | 4x1221 | 3.30 | AV1220 | 3.30 | 0 | 65535 |  |  | Maximum flow for Cooling Valve (if actuator supports flow measurements)
| ZoneModule 3 - VAV Extract2 Nominal Air Flow | m3/h | 4x1223 | 3.40 | AV1222 | 3.40 | 0 | 65535 |  |  | Zone 3 - Nominal air flow of the Extract2 actuator
| ZoneModule 3 - VAV Extract2 Min. Air Flow | m3/h | 4x1224 | 3.40 | AV1223 | 3.40 | 0 | 65535 |  |  | Zone 3 - Min. Extract2 air quantity [1/100 %]
| ZoneModule 3 - VAV Extract2 Max. Air Flow | m3/h | 4x1225 | 3.40 | AV1224 | 3.40 | 0 | 65535 |  |  | Zone 3 - Max. Extract2 air quantity [1/100 %]
0x3833 | ZoneModule 4 - Room Temperature Setpoint | °C | 4x1302 |  | AV1301 |  | 1000 | 4500 |  |  | Zone 4 - Setpoint for room temperature [1/100 °C]
0x3834 | ZoneModule 4 - Minimum Supply Temperature | °C | 4x1303 |  | AV1302 |  | 1000 | 3000 |  |  | Zone 4 - Setpoint for min. inlet temperature [1/100 °C]
0x3835 | ZoneModule 4 - Maximum Supply Temperature | °C | 4x1304 |  | AV1303 |  | 1000 | 6000 |  |  | Zone 4 - Setpoint for max. inlet temperature [1/100 °C]
0x3836 | ZoneModule 4 - Room CO2 Setpoint | ppm | 4x1305 |  | AV1304 |  | 100 | 5000 |  |  | Zone 4 - Setpoint for CO2 [ppm]
0x3837 | ZoneModule 4 - Room RH Setpoint | % | 4x1306 |  | AV1305 |  | 0 | 10000 |  |  | Zone 4 - Setpoint for relative humidity [1/100 %rh]
0x3838 | ZoneModule 4 - VAV Supply PIR Min. Air Flow | m3/h | 4x1307 |  | AV1306 |  | 0 | 65535 |  |  | Zone 4 - Min. inlet air quantity with PIR active [1/100 %]
0x3839 | ZoneModule 4 - VAV Supply 1 Min. Air Flow | m3/h | 4x1308 |  | AV1307 |  | 0 | 65535 |  |  | Zone 4 - Min. inlet air quantity, VAV damper 1 [1/100 %]
0x383A | ZoneModule 4 - VAV Supply 1 Max. Air Flow | m3/h | 4x1309 |  | AV1308 |  | 0 | 65535 |  |  | Zone 4 - Max. inlet air quantity, VAV damper 1 [1/100 %]
0x383B | ZoneModule 4 - VAV Supply 2 Min. Air Flow | m3/h | 4x1310 |  | AV1309 |  | 0 | 65535 |  |  | Zone 4 - Min. inlet air quantity, VAV damper 2 [1/100 %]
0x383C | ZoneModule 4 - VAV Supply 2 Max. Air Flow | m3/h | 4x1311 |  | AV1310 |  | 0 | 65535 |  |  | Zone 4 - Max. inlet air quantity, VAV damper 2 [1/100 %]
0x383D | ZoneModule 4 - VAV Extract Min. Air Flow | m3/h | 4x1312 |  | AV1311 |  | 0 | 65535 |  |  | Zone 4 - Min. exhaust air quantity [1/100 %]
0x383E | ZoneModule 4 - VAV Extract Max. Air Flow | m3/h | 4x1313 |  | AV1312 |  | 0 | 65535 |  |  | Zone 4 - Max. exhaust air quantity [1/100 %]
0x383F | ZoneModule 4 - VAV Supply 1 Nominal Air Flow | m3/h | 4x1314 | 3.30 | AV1313 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 1 actuator
0x3840 | ZoneModule 4 - VAV Supply 2 Nominal Air Flow | m3/h | 4x1315 | 3.30 | AV1314 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 2 actuator
0x3841 | ZoneModule 4 - VAV Extract Nominal Air Flow | m3/h | 4x1316 | 3.30 | AV1315 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Extract actuator
0x3842 | ZoneModule 4 - Room Panel Low Air Flow | % | 4x1317 | 3.30 | AV1316 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “Low”
0x3843 | ZoneModule 4 - Room Panel High Air Flow | % | 4x1318 | 3.30 | AV1317 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “High”
0x3844 | ZoneModule 4 - Room Panel Override Timeout | min | 4x1319 | 3.30 | AV1318 | 3.30 | 10 | 90 |  |  | Time in minutes after which override from RPT will be reset
0x3845 | ZoneModule 4 - Heat Valve Max. Flow | l/h | 4x1320 | 3.30 | AV1319 | 3.30 | 0 | 65535 |  |  | Maximum flow for Heating Valve (if actuator supports flow measurements)
0x3846 | ZoneModule 4 - Cool Valve Max. Flow | l/h | 4x1321 | 3.30 | AV1320 | 3.30 | 0 | 65535 |  |  | Maximum flow for Cooling Valve (if actuator supports flow measurements)
| ZoneModule 4 - VAV Extract2 Nominal Air Flow | m3/h | 4x1323 | 3.40 | AV1322 | 3.40 | 0 | 65535 |  |  | Zone 4 - Nominal air flow of the Extract2 actuator
| ZoneModule 4 - VAV Extract2 Min. Air Flow | m3/h | 4x1324 | 3.40 | AV1323 | 3.40 | 0 | 65535 |  |  | Zone 4 - Min. Extract2 air quantity [1/100 %]
| ZoneModule 4 - VAV Extract2 Max. Air Flow | m3/h | 4x1325 | 3.40 | AV1324 | 3.40 | 0 | 65535 |  |  | Zone 4 - Max. Extract2 air quantity [1/100 %]
0x3848 | ZoneModule 5 - Room Temperature Setpoint | °C | 4x1402 |  | AV1401 |  | 1000 | 4500 |  |  | Zone 5 - Setpoint for room temperature [1/100 °C]
0x3849 | ZoneModule 5 - Minimum Supply Temperature | °C | 4x1403 |  | AV1402 |  | 1000 | 3000 |  |  | Zone 5 - Setpoint for min. inlet temperature [1/100 °C]
0x384A | ZoneModule 5 - Maximum Supply Temperature | °C | 4x1404 |  | AV1403 |  | 1000 | 6000 |  |  | Zone 5 - Setpoint for max. inlet temperature [1/100 °C]
0x384B | ZoneModule 5 - Room CO2 Setpoint | ppm | 4x1405 |  | AV1404 |  | 100 | 5000 |  |  | Zone 5 - Setpoint for CO2 [ppm]
0x3850 | ZoneModule 5 - Room RH Setpoint | % | 4x1406 |  | AV1405 |  | 0 | 10000 |  |  | Zone 5 - Setpoint for relative humidity [1/100 %rh]
0x3851 | ZoneModule 5 - VAV Supply PIR Min. Air Flow | m3/h | 4x1407 |  | AV1406 |  | 0 | 65535 |  |  | Zone 5 - Min. inlet air quantity with PIR active [1/100 %]
0x3852 | ZoneModule 5 - VAV Supply 1 Min. Air Flow | m3/h | 4x1408 |  | AV1407 |  | 0 | 65535 |  |  | Zone 5 - Min. inlet air quantity, VAV damper 1 [1/100 %]
0x3853 | ZoneModule 5 - VAV Supply 1 Max. Air Flow | m3/h | 4x1409 |  | AV1408 |  | 0 | 65535 |  |  | Zone 5 - Max. inlet air quantity, VAV damper 1 [1/100 %]
0x3854 | ZoneModule 5 - VAV Supply 2 Min. Air Flow | m3/h | 4x1410 |  | AV1409 |  | 0 | 65535 |  |  | Zone 5 - Min. inlet air quantity, VAV damper 2 [1/100 %]
0x3855 | ZoneModule 5 - VAV Supply 2 Max. Air Flow | m3/h | 4x1411 |  | AV1410 |  | 0 | 65535 |  |  | Zone 5 - Max. inlet air quantity, VAV damper 2 [1/100 %]
0x3856 | ZoneModule 5 - VAV Extract Min. Air Flow | m3/h | 4x1412 |  | AV1411 |  | 0 | 65535 |  |  | Zone 5 - Min. exhaust air quantity [1/100 %]
0x3857 | ZoneModule 5 - VAV Extract Max. Air Flow | m3/h | 4x1413 |  | AV1412 |  | 0 | 65535 |  |  | Zone 5 - Max. exhaust air quantity [1/100 %]
0x3858 | ZoneModule 5 - VAV Supply 1 Nominal Air Flow | m3/h | 4x1414 | 3.30 | AV1413 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 1 actuator
0x3859 | ZoneModule 5 - VAV Supply 2 Nominal Air Flow | m3/h | 4x1415 | 3.30 | AV1414 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 2 actuator
0x385A | ZoneModule 5 - VAV Extract Nominal Air Flow | m3/h | 4x1416 | 3.30 | AV1415 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Extract actuator
0x385B | ZoneModule 5 - Room Panel Low Air Flow | % | 4x1417 | 3.30 | AV1416 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “Low”
0x385C | ZoneModule 5 - Room Panel High Air Flow | % | 4x1418 | 3.30 | AV1417 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “High”
0x385D | ZoneModule 5 - Room Panel Override Timeout | min | 4x1419 | 3.30 | AV1418 | 3.30 | 10 | 90 |  |  | Time in minutes after which override from RPT will be reset
0x385E | ZoneModule 5 - Heat Valve Max. Flow | l/h | 4x1420 | 3.30 | AV1419 | 3.30 | 0 | 65535 |  |  | Maximum flow for Heating Valve (if actuator supports flow measurements)
0x385F | ZoneModule 5 - Cool Valve Max. Flow | l/h | 4x1421 | 3.30 | AV1420 | 3.30 | 0 | 65535 |  |  | Maximum flow for Cooling Valve (if actuator supports flow measurements)
| ZoneModule 5 - VAV Extract2 Nominal Air Flow | m3/h | 4x1423 | 3.40 | AV1422 | 3.40 | 0 | 65535 |  |  | Zone 5 - Nominal air flow of the Extract2 actuator
| ZoneModule 5 - VAV Extract2 Min. Air Flow | m3/h | 4x1424 | 3.40 | AV1423 | 3.40 | 0 | 65535 |  |  | Zone 5 - Min. Extract2 air quantity [1/100 %]
| ZoneModule 5 - VAV Extract2 Max. Air Flow | m3/h | 4x1425 | 3.40 | AV1424 | 3.40 | 0 | 65535 |  |  | Zone 5 - Max. Extract2 air quantity [1/100 %]
0x3861 | ZoneModule 6 - Room Temperature Setpoint | °C | 4x1502 |  | AV1501 |  | 1000 | 4500 |  |  | Zone 6 - Setpoint for room temperature [1/100 °C]
0x3862 | ZoneModule 6 - Minimum Supply Temperature | °C | 4x1503 |  | AV1502 |  | 1000 | 3000 |  |  | Zone 6 - Setpoint for min. inlet temperature [1/100 °C]
0x3863 | ZoneModule 6 - Maximum Supply Temperature | °C | 4x1504 |  | AV1503 |  | 1000 | 6000 |  |  | Zone 6 - Setpoint for max. inlet temperature [1/100 °C]
0x3864 | ZoneModule 6 - Room CO2 Setpoint | ppm | 4x1505 |  | AV1504 |  | 100 | 5000 |  |  | Zone 6 - Setpoint for CO2 [ppm]
0x3865 | ZoneModule 6 - Room RH Setpoint | % | 4x1506 |  | AV1505 |  | 0 | 10000 |  |  | Zone 6 - Setpoint for relative humidity [1/100 %rh]
0x3866 | ZoneModule 6 - VAV Supply PIR Min. Air Flow | m3/h | 4x1507 |  | AV1506 |  | 0 | 65535 |  |  | Zone 6 - Min. inlet air quantity with PIR active [1/100 %]
0x3867 | ZoneModule 6 - VAV Supply 1 Min. Air Flow | m3/h | 4x1508 |  | AV1507 |  | 0 | 65535 |  |  | Zone 6 - Min. inlet air quantity, VAV damper 1 [1/100 %]
0x3868 | ZoneModule 6 - VAV Supply 1 Max. Air Flow | m3/h | 4x1509 |  | AV1508 |  | 0 | 65535 |  |  | Zone 6 - Max. inlet air quantity, VAV damper 1 [1/100 %]
0x3869 | ZoneModule 6 - VAV Supply 2 Min. Air Flow | m3/h | 4x1510 |  | AV1509 |  | 0 | 65535 |  |  | Zone 6 - Min. inlet air quantity, VAV damper 2 [1/100 %]
0x386A | ZoneModule 6 - VAV Supply 2 Max. Air Flow | m3/h | 4x1511 |  | AV1510 |  | 0 | 65535 |  |  | Zone 6 - Max. inlet air quantity, VAV damper 2 [1/100 %]
0x386B | ZoneModule 6 - VAV Extract Min. Air Flow | m3/h | 4x1512 |  | AV1511 |  | 0 | 65535 |  |  | Zone 6 - Min. exhaust air quantity [1/100 %]
0x3460 | ZoneModule 6 - VAV Extract Max. Air Flow | m3/h | 4x1513 |  | AV1512 |  | 0 | 65535 |  |  | Zone 6 - Max. exhaust air quantity [1/100 %]
0x3461 | ZoneModule 6 - VAV Supply 1 Nominal Air Flow | m3/h | 4x1514 | 3.30 | AV1513 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 1 actuator
0x3101 | ZoneModule 6 - VAV Supply 2 Nominal Air Flow | m3/h | 4x1515 | 3.30 | AV1514 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 2 actuator
0x3102 | ZoneModule 6 - VAV Extract Nominal Air Flow | m3/h | 4x1516 | 3.30 | AV1515 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Extract actuator
0x3103 | ZoneModule 6 - Room Panel Low Air Flow | % | 4x1517 | 3.30 | AV1516 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “Low”
0x3108 | ZoneModule 6 - Room Panel High Air Flow | % | 4x1518 | 3.30 | AV1517 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “High”
0x3110 | ZoneModule 6 - Room Panel Override Timeout | min | 4x1519 | 3.30 | AV1518 | 3.30 | 10 | 90 |  |  | Time in minutes after which override from RPT will be reset
0x3111 | ZoneModule 6 - Heat Valve Max. Flow | l/h | 4x1520 | 3.30 | AV1519 | 3.30 | 0 | 65535 |  |  | Maximum flow for Heating Valve (if actuator supports flow measurements)
0x3112 | ZoneModule 6 - Cool Valve Max. Flow | l/h | 4x1521 | 3.30 | AV1520 | 3.30 | 0 | 65535 |  |  | Maximum flow for Cooling Valve (if actuator supports flow measurements)
| ZoneModule 6 - VAV Extract2 Nominal Air Flow | m3/h | 4x1523 | 3.40 | AV1522 | 3.40 | 0 | 65535 |  |  | Zone 6 - Nominal air flow of the Extract2 actuator
| ZoneModule 6 - VAV Extract2 Min. Air Flow | m3/h | 4x1524 | 3.40 | AV1523 | 3.40 | 0 | 65535 |  |  | Zone 6 - Min. Extract2 air quantity [1/100 %]
| ZoneModule 6 - VAV Extract2 Max. Air Flow | m3/h | 4x1525 | 3.40 | AV1524 | 3.40 | 0 | 65535 |  |  | Zone 6 - Max. Extract2 air quantity [1/100 %]
0x3114 | ZoneModule 7 - Room Temperature Setpoint | °C | 4x1602 |  | AV1601 |  | 1000 | 4500 |  |  | Zone 7 - Setpoint for room temperature [1/100 °C]
0x3105 | ZoneModule 7 - Minimum Supply Temperature | °C | 4x1603 |  | AV1602 |  | 1000 | 3000 |  |  | Zone 7 - Setpoint for min. inlet temperature [1/100 °C]
0x3109 | ZoneModule 7 - Maximum Supply Temperature | °C | 4x1604 |  | AV1603 |  | 1000 | 6000 |  |  | Zone 7 - Setpoint for max. inlet temperature [1/100 °C]
0x3208 | ZoneModule 7 - Room CO2 Setpoint | ppm | 4x1605 |  | AV1604 |  | 100 | 5000 |  |  | Zone 7 - Setpoint for CO2 [ppm]
0x3210 | ZoneModule 7 - Room RH Setpoint | % | 4x1606 |  | AV1605 |  | 0 | 10000 |  |  | Zone 7 - Setpoint for relative humidity [1/100 %rh]
0x3211 | ZoneModule 7 - VAV Supply PIR Min. Air Flow | m3/h | 4x1607 |  | AV1606 |  | 0 | 65535 |  |  | Zone 7 - Min. inlet air quantity with PIR active [1/100 %]
0x3212 | ZoneModule 7 - VAV Supply 1 Min. Air Flow | m3/h | 4x1608 |  | AV1607 |  | 0 | 65535 |  |  | Zone 7 - Min. inlet air quantity, VAV damper 1 [1/100 %]
0x3213 | ZoneModule 7 - VAV Supply 1 Max. Air Flow | m3/h | 4x1609 |  | AV1608 |  | 0 | 65535 |  |  | Zone 7 - Max. inlet air quantity, VAV damper 1 [1/100 %]
0x3214 | ZoneModule 7 - VAV Supply 2 Min. Air Flow | m3/h | 4x1610 |  | AV1609 |  | 0 | 65535 |  |  | Zone 7 - Min. inlet air quantity, VAV damper 2 [1/100 %]
0x3215 | ZoneModule 7 - VAV Supply 2 Max. Air Flow | m3/h | 4x1611 |  | AV1610 |  | 0 | 65535 |  |  | Zone 7 - Max. inlet air quantity, VAV damper 2 [1/100 %]
0x3209 | ZoneModule 7 - VAV Extract Min. Air Flow | m3/h | 4x1612 |  | AV1611 |  | 0 | 65535 |  |  | Zone 7 - Min. exhaust air quantity [1/100 %]
0x3380 | ZoneModule 7 - VAV Extract Max. Air Flow | m3/h | 4x1613 |  | AV1612 |  | 0 | 65535 |  |  | Zone 7 - Max. exhaust air quantity [1/100 %]
0x3381 | ZoneModule 7 - VAV Supply 1 Nominal Air Flow | m3/h | 4x1614 | 3.30 | AV1613 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 1 actuator
0x3382 | ZoneModule 7 - VAV Supply 2 Nominal Air Flow | m3/h | 4x1615 | 3.30 | AV1614 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 2 actuator
0x3383 | ZoneModule 7 - VAV Extract Nominal Air Flow | m3/h | 4x1616 | 3.30 | AV1615 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Extract actuator
0x3384 | ZoneModule 7 - Room Panel Low Air Flow | % | 4x1617 | 3.30 | AV1616 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “Low”
0x3385 | ZoneModule 7 - Room Panel High Air Flow | % | 4x1618 | 3.30 | AV1617 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “High”
0x33D0 | ZoneModule 7 - Room Panel Override Timeout | min | 4x1619 | 3.30 | AV1618 | 3.30 | 10 | 90 |  |  | Time in minutes after which override from RPT will be reset
0x33D1 | ZoneModule 7 - Heat Valve Max. Flow | l/h | 4x1620 | 3.30 | AV1619 | 3.30 | 0 | 65535 |  |  | Maximum flow for Heating Valve (if actuator supports flow measurements)
0x33D2 | ZoneModule 7 - Cool Valve Max. Flow | l/h | 4x1621 | 3.30 | AV1620 | 3.30 | 0 | 65535 |  |  | Maximum flow for Cooling Valve (if actuator supports flow measurements)
| ZoneModule 7 - VAV Extract2 Nominal Air Flow | m3/h | 4x1623 | 3.40 | AV1622 | 3.40 | 0 | 65535 |  |  | Zone 7 - Nominal air flow of the Extract2 actuator
| ZoneModule 7 - VAV Extract2 Min. Air Flow | m3/h | 4x1624 | 3.40 | AV1623 | 3.40 | 0 | 65535 |  |  | Zone 7 - Min. Extract2 air quantity [1/100 %]
| ZoneModule 7 - VAV Extract2 Max. Air Flow | m3/h | 4x1625 | 3.40 | AV1624 | 3.40 | 0 | 65535 |  |  | Zone 7 - Max. Extract2 air quantity [1/100 %]
0x33D4 | ZoneModule 8 - Room Temperature Setpoint | °C | 4x1702 |  | AV1701 |  | 1000 | 4500 |  |  | Zone 8 - Setpoint for room temperature [1/100 °C]
0x33D5 | ZoneModule 8 - Minimum Supply Temperature | °C | 4x1703 |  | AV1702 |  | 1000 | 3000 |  |  | Zone 8 - Setpoint for min. inlet temperature [1/100 °C]
0x33D6 | ZoneModule 8 - Maximum Supply Temperature | °C | 4x1704 |  | AV1703 |  | 1000 | 6000 |  |  | Zone 8 - Setpoint for max. inlet temperature [1/100 °C]
0x33E0 | ZoneModule 8 - Room CO2 Setpoint | ppm | 4x1705 |  | AV1704 |  | 100 | 5000 |  |  | Zone 8 - Setpoint for CO2 [ppm]
0x33E1 | ZoneModule 8 - Room RH Setpoint | % | 4x1706 |  | AV1705 |  | 0 | 10000 |  |  | Zone 8 - Setpoint for relative humidity [1/100 %rh]
0x3104 | ZoneModule 8 - VAV Supply PIR Min. Air Flow | m3/h | 4x1707 |  | AV1706 |  | 0 | 65535 |  |  | Zone 8 - Min. inlet air quantity with PIR active [1/100 %]
0x3204 | ZoneModule 8 - VAV Supply 1 Min. Air Flow | m3/h | 4x1708 |  | AV1707 |  | 0 | 65535 |  |  | Zone 8 - Min. inlet air quantity, VAV damper 1 [1/100 %]
0x3420 | ZoneModule 8 - VAV Supply 1 Max. Air Flow | m3/h | 4x1709 |  | AV1708 |  | 0 | 65535 |  |  | Zone 8 - Max. inlet air quantity, VAV damper 1 [1/100 %]
0x3421 | ZoneModule 8 - VAV Supply 2 Min. Air Flow | m3/h | 4x1710 |  | AV1709 |  | 0 | 65535 |  |  | Zone 8 - Min. inlet air quantity, VAV damper 2 [1/100 %]
0x3422 | ZoneModule 8 - VAV Supply 2 Max. Air Flow | m3/h | 4x1711 |  | AV1710 |  | 0 | 65535 |  |  | Zone 8 - Max. inlet air quantity, VAV damper 2 [1/100 %]
0x3370 | ZoneModule 8 - VAV Extract Min. Air Flow | m3/h | 4x1712 |  | AV1711 |  | 0 | 65535 |  |  | Zone 8 - Min. exhaust air quantity [1/100 %]
0x3371 | ZoneModule 8 - VAV Extract Max. Air Flow | m3/h | 4x1713 |  | AV1712 |  | 0 | 65535 |  |  | Zone 8 - Max. exhaust air quantity [1/100 %]
0x3372 | ZoneModule 8 - VAV Supply 1 Nominal Air Flow | m3/h | 4x1714 | 3.30 | AV1713 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 1 actuator
0x3373 | ZoneModule 8 - VAV Supply 2 Nominal Air Flow | m3/h | 4x1715 | 3.30 | AV1714 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 2 actuator
0x3374 | ZoneModule 8 - VAV Extract Nominal Air Flow | m3/h | 4x1716 | 3.30 | AV1715 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Extract actuator
0x3375 | ZoneModule 8 - Room Panel Low Air Flow | % | 4x1717 | 3.30 | AV1716 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “Low”
0x3320 | ZoneModule 8 - Room Panel High Air Flow | % | 4x1718 | 3.30 | AV1717 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “High”
0x3321 | ZoneModule 8 - Room Panel Override Timeout | min | 4x1719 | 3.30 | AV1718 | 3.30 | 10 | 90 |  |  | Time in minutes after which override from RPT will be reset
0x3323 | ZoneModule 8 - Heat Valve Max. Flow | l/h | 4x1720 | 3.30 | AV1719 | 3.30 | 0 | 65535 |  |  | Maximum flow for Heating Valve (if actuator supports flow measurements)
0x3324 | ZoneModule 8 - Cool Valve Max. Flow | l/h | 4x1721 | 3.30 | AV1720 | 3.30 | 0 | 65535 |  |  | Maximum flow for Cooling Valve (if actuator supports flow measurements)
| ZoneModule 8 - VAV Extract2 Nominal Air Flow | m3/h | 4x1723 | 3.40 | AV1722 | 3.40 | 0 | 65535 |  |  | Zone 8 - Nominal air flow of the Extract2 actuator
| ZoneModule 8 - VAV Extract2 Min. Air Flow | m3/h | 4x1724 | 3.40 | AV1723 | 3.40 | 0 | 65535 |  |  | Zone 8 - Min. Extract2 air quantity [1/100 %]
| ZoneModule 8 - VAV Extract2 Max. Air Flow | m3/h | 4x1725 | 3.40 | AV1724 | 3.40 | 0 | 65535 |  |  | Zone 8 - Max. Extract2 air quantity [1/100 %]
0x3921 | ZoneModule 9 - Room Temperature Setpoint | °C | 4x1802 |  | AV1801 |  | 1000 | 4500 |  |  | Zone 9 - Setpoint for room temperature [1/100 °C]
0x3922 | ZoneModule 9 - Minimum Supply Temperature | °C | 4x1803 |  | AV1802 |  | 1000 | 3000 |  |  | Zone 9 - Setpoint for min. inlet temperature [1/100 °C]
0x3478 | ZoneModule 9 - Maximum Supply Temperature | °C | 4x1804 |  | AV1803 |  | 1000 | 6000 |  |  | Zone 9 - Setpoint for max. inlet temperature [1/100 °C]
0x3330 | ZoneModule 9 - Room CO2 Setpoint | ppm | 4x1805 |  | AV1804 |  | 100 | 5000 |  |  | Zone 9 - Setpoint for CO2 [ppm]
0x3331 | ZoneModule 9 - Room RH Setpoint | % | 4x1806 |  | AV1805 |  | 0 | 10000 |  |  | Zone 9 - Setpoint for relative humidity [1/100 %rh]
0x3332 | ZoneModule 9 - VAV Supply PIR Min. Air Flow | m3/h | 4x1807 |  | AV1806 |  | 0 | 65535 |  |  | Zone 9 - Min. inlet air quantity with PIR active [1/100 %]
0x3333 | ZoneModule 9 - VAV Supply 1 Min. Air Flow | m3/h | 4x1808 |  | AV1807 |  | 0 | 65535 |  |  | Zone 9 - Min. inlet air quantity, VAV damper 1 [1/100 %]
0x3334 | ZoneModule 9 - VAV Supply 1 Max. Air Flow | m3/h | 4x1809 |  | AV1808 |  | 0 | 65535 |  |  | Zone 9 - Max. inlet air quantity, VAV damper 1 [1/100 %]
0x3335 | ZoneModule 9 - VAV Supply 2 Min. Air Flow | m3/h | 4x1810 |  | AV1809 |  | 0 | 65535 |  |  | Zone 9 - Min. inlet air quantity, VAV damper 2 [1/100 %]
0x3336 | ZoneModule 9 - VAV Supply 2 Max. Air Flow | m3/h | 4x1811 |  | AV1810 |  | 0 | 65535 |  |  | Zone 9 - Max. inlet air quantity, VAV damper 2 [1/100 %]
0x333C | ZoneModule 9 - VAV Extract Min. Air Flow | m3/h | 4x1812 |  | AV1811 |  | 0 | 65535 |  |  | Zone 9 - Min. exhaust air quantity [1/100 %]
0x3350 | ZoneModule 9 - VAV Extract Max. Air Flow | m3/h | 4x1813 |  | AV1812 |  | 0 | 65535 |  |  | Zone 9 - Max. exhaust air quantity [1/100 %]
0x3351 | ZoneModule 9 - VAV Supply 1 Nominal Air Flow | m3/h | 4x1814 | 3.30 | AV1813 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 1 actuator
0x3475 | ZoneModule 9 - VAV Supply 2 Nominal Air Flow | m3/h | 4x1815 | 3.30 | AV1814 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 2 actuator
0x3476 | ZoneModule 9 - VAV Extract Nominal Air Flow | m3/h | 4x1816 | 3.30 | AV1815 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Extract actuator
0x3390 | ZoneModule 9 - Room Panel Low Air Flow | % | 4x1817 | 3.30 | AV1816 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “Low”
0x3391 | ZoneModule 9 - Room Panel High Air Flow | % | 4x1818 | 3.30 | AV1817 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “High”
0x3392 | ZoneModule 9 - Room Panel Override Timeout | min | 4x1819 | 3.30 | AV1818 | 3.30 | 10 | 90 |  |  | Time in minutes after which override from RPT will be reset
0x3393 | ZoneModule 9 - Heat Valve Max. Flow | l/h | 4x1820 | 3.30 | AV1819 | 3.30 | 0 | 65535 |  |  | Maximum flow for Heating Valve (if actuator supports flow measurements)
0x339B | ZoneModule 9 - Cool Valve Max. Flow | l/h | 4x1821 | 3.30 | AV1820 | 3.30 | 0 | 65535 |  |  | Maximum flow for Cooling Valve (if actuator supports flow measurements)
| ZoneModule 9 - VAV Extract2 Nominal Air Flow | m3/h | 4x1823 | 3.40 | AV1822 | 3.40 | 0 | 65535 |  |  | Zone 9 - Nominal air flow of the Extract2 actuator
| ZoneModule 9 - VAV Extract2 Min. Air Flow | m3/h | 4x1824 | 3.40 | AV1823 | 3.40 | 0 | 65535 |  |  | Zone 9 - Min. Extract2 air quantity [1/100 %]
| ZoneModule 9 - VAV Extract2 Max. Air Flow | m3/h | 4x1825 | 3.40 | AV1824 | 3.40 | 0 | 65535 |  |  | Zone 9 - Max. Extract2 air quantity [1/100 %]
0x3005 | ZoneModule 10 - Room Temperature Setpoint | °C | 4x1902 |  | AV1901 |  | 1000 | 4500 |  |  | Zone 10 - Setpoint for room temperature [1/100 °C]
0x34C5 | ZoneModule 10 - Minimum Supply Temperature | °C | 4x1903 |  | AV1902 |  | 1000 | 3000 |  |  | Zone 10 - Setpoint for min. inlet temperature [1/100 °C]
0x34CC | ZoneModule 10 - Maximum Supply Temperature | °C | 4x1904 |  | AV1903 |  | 1000 | 6000 |  |  | Zone 10 - Setpoint for max. inlet temperature [1/100 °C]
0x34CB | ZoneModule 10 - Room CO2 Setpoint | ppm | 4x1905 |  | AV1904 |  | 100 | 5000 |  |  | Zone 10 - Setpoint for CO2 [ppm]
0x34C4 | ZoneModule 10 - Room RH Setpoint | % | 4x1906 |  | AV1905 |  | 0 | 10000 |  |  | Zone 10 - Setpoint for relative humidity [1/100 %rh]
0x34CE | ZoneModule 10 - VAV Supply PIR Min. Air Flow | m3/h | 4x1907 |  | AV1906 |  | 0 | 65535 |  |  | Zone 10 - Min. inlet air quantity with PIR active [1/100 %]
0x34C8 | ZoneModule 10 - VAV Supply 1 Min. Air Flow | m3/h | 4x1908 |  | AV1907 |  | 0 | 65535 |  |  | Zone 10 - Min. inlet air quantity, VAV damper 1 [1/100 %]
0x34C3 | ZoneModule 10 - VAV Supply 1 Max. Air Flow | m3/h | 4x1909 |  | AV1908 |  | 0 | 65535 |  |  | Zone 10 - Max. inlet air quantity, VAV damper 1 [1/100 %]
0x34C2 | ZoneModule 10 - VAV Supply 2 Min. Air Flow | m3/h | 4x1910 |  | AV1909 |  | 0 | 65535 |  |  | Zone 10 - Min. inlet air quantity, VAV damper 2 [1/100 %]
0x3400 | ZoneModule 10 - VAV Supply 2 Max. Air Flow | m3/h | 4x1911 |  | AV1910 |  | 0 | 65535 |  |  | Zone 10 - Max. inlet air quantity, VAV damper 2 [1/100 %]
0x3401 | ZoneModule 10 - VAV Extract Min. Air Flow | m3/h | 4x1912 |  | AV1911 |  | 0 | 65535 |  |  | Zone 10 - Min. exhaust air quantity [1/100 %]
0x3402 | ZoneModule 10 - VAV Extract Max. Air Flow | m3/h | 4x1913 |  | AV1912 |  | 0 | 65535 |  |  | Zone 10 - Max. exhaust air quantity [1/100 %]
0x340C | ZoneModule 10 - VAV Supply 1 Nominal Air Flow | m3/h | 4x1914 | 3.30 | AV1913 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 1 actuator
0x3403 | ZoneModule 10 - VAV Supply 2 Nominal Air Flow | m3/h | 4x1915 | 3.30 | AV1914 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 2 actuator
0x3404 | ZoneModule 10 - VAV Extract Nominal Air Flow | m3/h | 4x1916 | 3.30 | AV1915 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Extract actuator
0x3405 | ZoneModule 10 - Room Panel Low Air Flow | % | 4x1917 | 3.30 | AV1916 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “Low”
0x3406 | ZoneModule 10 - Room Panel High Air Flow | % | 4x1918 | 3.30 | AV1917 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “High”
0x3352 | ZoneModule 10 - Room Panel Override Timeout | min | 4x1919 | 3.30 | AV1918 | 3.30 | 10 | 90 |  |  | Time in minutes after which override from RPT will be reset
0x3923 | ZoneModule 10 - Heat Valve Max. Flow | l/h | 4x1920 | 3.30 | AV1919 | 3.30 | 0 | 65535 |  |  | Maximum flow for Heating Valve (if actuator supports flow measurements)
0x3358 | ZoneModule 10 - Cool Valve Max. Flow | l/h | 4x1921 | 3.30 | AV1920 | 3.30 | 0 | 65535 |  |  | Maximum flow for Cooling Valve (if actuator supports flow measurements)
| ZoneModule 10 - VAV Extract2 Nominal Air Flow | m3/h | 4x1923 | 3.40 | AV1922 | 3.40 | 0 | 65535 |  |  | Zone 10 - Nominal air flow of the Extract2 actuator
| ZoneModule 10 - VAV Extract2 Min. Air Flow | m3/h | 4x1924 | 3.40 | AV1923 | 3.40 | 0 | 65535 |  |  | Zone 10 - Min. Extract2 air quantity [1/100 %]
| ZoneModule 10 - VAV Extract2 Max. Air Flow | m3/h | 4x1925 | 3.40 | AV1924 | 3.40 | 0 | 65535 |  |  | Zone 10 - Max. Extract2 air quantity [1/100 %]
0x335A | ZoneModule 11 - Room Temperature Setpoint | °C | 4x2002 |  | AV2001 |  | 1000 | 4500 |  |  | Zone 11 - Setpoint for room temperature [1/100 °C]
0x335B | ZoneModule 11 - Minimum Supply Temperature | °C | 4x2003 |  | AV2002 |  | 1000 | 3000 |  |  | Zone 11 - Setpoint for min. inlet temperature [1/100 °C]
0x3410 | ZoneModule 11 - Maximum Supply Temperature | °C | 4x2004 |  | AV2003 |  | 1000 | 6000 |  |  | Zone 11 - Setpoint for max. inlet temperature [1/100 °C]
0x3411 | ZoneModule 11 - Room CO2 Setpoint | ppm | 4x2005 |  | AV2004 |  | 100 | 5000 |  |  | Zone 11 - Setpoint for CO2 [ppm]
0x3412 | ZoneModule 11 - Room RH Setpoint | % | 4x2006 |  | AV2005 |  | 0 | 10000 |  |  | Zone 11 - Setpoint for relative humidity [1/100 %rh]
0x341C | ZoneModule 11 - VAV Supply PIR Min. Air Flow | m3/h | 4x2007 |  | AV2006 |  | 0 | 65535 |  |  | Zone 11 - Min. inlet air quantity with PIR active [1/100 %]
0x3413 | ZoneModule 11 - VAV Supply 1 Min. Air Flow | m3/h | 4x2008 |  | AV2007 |  | 0 | 65535 |  |  | Zone 11 - Min. inlet air quantity, VAV damper 1 [1/100 %]
0x3414 | ZoneModule 11 - VAV Supply 1 Max. Air Flow | m3/h | 4x2009 |  | AV2008 |  | 0 | 65535 |  |  | Zone 11 - Max. inlet air quantity, VAV damper 1 [1/100 %]
0x3415 | ZoneModule 11 - VAV Supply 2 Min. Air Flow | m3/h | 4x2010 |  | AV2009 |  | 0 | 65535 |  |  | Zone 11 - Min. inlet air quantity, VAV damper 2 [1/100 %]
0x3416 | ZoneModule 11 - VAV Supply 2 Max. Air Flow | m3/h | 4x2011 |  | AV2010 |  | 0 | 65535 |  |  | Zone 11 - Max. inlet air quantity, VAV damper 2 [1/100 %]
0x3925 | ZoneModule 11 - VAV Extract Min. Air Flow | m3/h | 4x2012 |  | AV2011 |  | 0 | 65535 |  |  | Zone 11 - Min. exhaust air quantity [1/100 %]
0x3926 | ZoneModule 11 - VAV Extract Max. Air Flow | m3/h | 4x2013 |  | AV2012 |  | 0 | 65535 |  |  | Zone 11 - Max. exhaust air quantity [1/100 %]
0x3927 | ZoneModule 11 - VAV Supply 1 Nominal Air Flow | m3/h | 4x2014 | 3.30 | AV2013 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 1 actuator
0x3928 | ZoneModule 11 - VAV Supply 2 Nominal Air Flow | m3/h | 4x2015 | 3.30 | AV2014 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 2 actuator
0x23A7 | ZoneModule 11 - VAV Extract Nominal Air Flow | m3/h | 4x2016 | 3.30 | AV2015 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Extract actuator
0x33DA | ZoneModule 11 - Room Panel Low Air Flow | % | 4x2017 | 3.30 | AV2016 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “Low”
0x2418 | ZoneModule 11 - Room Panel High Air Flow | % | 4x2018 | 3.30 | AV2017 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “High”
0x34F2 | ZoneModule 11 - Room Panel Override Timeout | min | 4x2019 | 3.30 | AV2018 | 3.30 | 10 | 90 |  |  | Time in minutes after which override from RPT will be reset
0x34F3 | ZoneModule 11 - Heat Valve Max. Flow | l/h | 4x2020 | 3.30 | AV2019 | 3.30 | 0 | 65535 |  |  | Maximum flow for Heating Valve (if actuator supports flow measurements)
0x34F4 | ZoneModule 11 - Cool Valve Max. Flow | l/h | 4x2021 | 3.30 | AV2020 | 3.30 | 0 | 65535 |  |  | Maximum flow for Cooling Valve (if actuator supports flow measurements)
| ZoneModule 11 - VAV Extract2 Nominal Air Flow | m3/h | 4x2023 | 3.40 | AV2022 | 3.40 | 0 | 65535 |  |  | Zone 11 - Nominal air flow of the Extract2 actuator
| ZoneModule 11 - VAV Extract2 Min. Air Flow | m3/h | 4x2024 | 3.40 | AV2023 | 3.40 | 0 | 65535 |  |  | Zone 11 - Min. Extract2 air quantity [1/100 %]
| ZoneModule 11 - VAV Extract2 Max. Air Flow | m3/h | 4x2025 | 3.41 | AV2024 | 3.40 | 0 | 65535 |  |  | Zone 11 - Max. Extract2 air quantity [1/100 %]
0x34F6 | ZoneModule 12 - Room Temperature Setpoint | °C | 4x2102 |  | AV2101 |  | 1000 | 4500 |  |  | Zone 12 - Setpoint for room temperature [1/100 °C]
0x34F7 | ZoneModule 12 - Minimum Supply Temperature | °C | 4x2103 |  | AV2102 |  | 1000 | 3000 |  |  | Zone 12 - Setpoint for min. inlet temperature [1/100 °C]
0x34F1 | ZoneModule 12 - Maximum Supply Temperature | °C | 4x2104 |  | AV2103 |  | 1000 | 6000 |  |  | Zone 12 - Setpoint for max. inlet temperature [1/100 °C]
0x3A8E | ZoneModule 12 - Room CO2 Setpoint | ppm | 4x2105 |  | AV2104 |  | 100 | 5000 |  |  | Zone 12 - Setpoint for CO2 [ppm]
0x34F0 | ZoneModule 12 - Room RH Setpoint | % | 4x2106 |  | AV2105 |  | 0 | 10000 |  |  | Zone 12 - Setpoint for relative humidity [1/100 %rh]
0x3488 | ZoneModule 12 - VAV Supply PIR Min. Air Flow | m3/h | 4x2107 |  | AV2106 |  | 0 | 65535 |  |  | Zone 12 - Min. inlet air quantity with PIR active [1/100 %]
0x34F8 | ZoneModule 12 - VAV Supply 1 Min. Air Flow | m3/h | 4x2108 |  | AV2107 |  | 0 | 65535 |  |  | Zone 12 - Min. inlet air quantity, VAV damper 1 [1/100 %]
0x34F9 | ZoneModule 12 - VAV Supply 1 Max. Air Flow | m3/h | 4x2109 |  | AV2108 |  | 0 | 65535 |  |  | Zone 12 - Max. inlet air quantity, VAV damper 1 [1/100 %]
0x3A9E | ZoneModule 12 - VAV Supply 2 Min. Air Flow | m3/h | 4x2110 |  | AV2109 |  | 0 | 65535 |  |  | Zone 12 - Min. inlet air quantity, VAV damper 2 [1/100 %]
0x3A9F | ZoneModule 12 - VAV Supply 2 Max. Air Flow | m3/h | 4x2111 |  | AV2110 |  | 0 | 65535 |  |  | Zone 12 - Max. inlet air quantity, VAV damper 2 [1/100 %]
0x33DB | ZoneModule 12 - VAV Extract Min. Air Flow | m3/h | 4x2112 |  | AV2111 |  | 0 | 65535 |  |  | Zone 12 - Min. exhaust air quantity [1/100 %]
0x32F5 | ZoneModule 12 - VAV Extract Max. Air Flow | m3/h | 4x2113 |  | AV2112 |  | 0 | 65535 |  |  | Zone 12 - Max. exhaust air quantity [1/100 %]
0x33C8 | ZoneModule 12 - VAV Supply 1 Nominal Air Flow | m3/h | 4x2114 | 3.30 | AV2113 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 1 actuator
0x33C9 | ZoneModule 12 - VAV Supply 2 Nominal Air Flow | m3/h | 4x2115 | 3.30 | AV2114 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 2 actuator
0x33CA | ZoneModule 12 - VAV Extract Nominal Air Flow | m3/h | 4x2116 | 3.30 | AV2115 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Extract actuator
0x33CB | ZoneModule 12 - Room Panel Low Air Flow | % | 4x2117 | 3.30 | AV2116 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “Low”
0x33CC | ZoneModule 12 - Room Panel High Air Flow | % | 4x2118 | 3.30 | AV2117 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “High”
0x33CD | ZoneModule 12 - Room Panel Override Timeout | min | 4x2119 | 3.30 | AV2118 | 3.30 | 10 | 90 |  |  | Time in minutes after which override from RPT will be reset
0x33CE | ZoneModule 12 - Heat Valve Max. Flow | l/h | 4x2120 | 3.30 | AV2119 | 3.30 | 0 | 65535 |  |  | Maximum flow for Heating Valve (if actuator supports flow measurements)
0x345B | ZoneModule 12 - Cool Valve Max. Flow | l/h | 4x2121 | 3.30 | AV2120 | 3.30 | 0 | 65535 |  |  | Maximum flow for Cooling Valve (if actuator supports flow measurements)
| ZoneModule 12 - VAV Extract2 Nominal Air Flow | m3/h | 4x2123 | 3.40 | AV2122 | 3.40 | 0 | 65535 |  |  | Zone 12 - Nominal air flow of the Extract2 actuator
| ZoneModule 12 - VAV Extract2 Min. Air Flow | m3/h | 4x2124 | 3.40 | AV2123 | 3.40 | 0 | 65535 |  |  | Zone 12 - Min. Extract2 air quantity [1/100 %]
| ZoneModule 12 - VAV Extract2 Max. Air Flow | m3/h | 4x2125 | 3.40 | AV2124 | 3.40 | 0 | 65535 |  |  | Zone 12 - Max. Extract2 air quantity [1/100 %]
0x3123 | ZoneModule 13 - Room Temperature Setpoint | °C | 4x2202 |  | AV2201 |  | 1000 | 4500 |  |  | Zone 13 - Setpoint for room temperature [1/100 °C]
0x3223 | ZoneModule 13 - Minimum Supply Temperature | °C | 4x2203 |  | AV2202 |  | 1000 | 3000 |  |  | Zone 13 - Setpoint for min. inlet temperature [1/100 °C]
0x316D | ZoneModule 13 - Maximum Supply Temperature | °C | 4x2204 |  | AV2203 |  | 1000 | 6000 |  |  | Zone 13 - Setpoint for max. inlet temperature [1/100 °C]
0x316E | ZoneModule 13 - Room CO2 Setpoint | ppm | 4x2205 |  | AV2204 |  | 100 | 5000 |  |  | Zone 13 - Setpoint for CO2 [ppm]
0x326D | ZoneModule 13 - Room RH Setpoint | % | 4x2206 |  | AV2205 |  | 0 | 10000 |  |  | Zone 13 - Setpoint for relative humidity [1/100 %rh]
0x346C | ZoneModule 13 - VAV Supply PIR Min. Air Flow | m3/h | 4x2207 |  | AV2206 |  | 0 | 65535 |  |  | Zone 13 - Min. inlet air quantity with PIR active [1/100 %]
0x33ED | ZoneModule 13 - VAV Supply 1 Min. Air Flow | m3/h | 4x2208 |  | AV2207 |  | 0 | 65535 |  |  | Zone 13 - Min. inlet air quantity, VAV damper 1 [1/100 %]
0x339C | ZoneModule 13 - VAV Supply 1 Max. Air Flow | m3/h | 4x2209 |  | AV2208 |  | 0 | 65535 |  |  | Zone 13 - Max. inlet air quantity, VAV damper 1 [1/100 %]
0x339D | ZoneModule 13 - VAV Supply 2 Min. Air Flow | m3/h | 4x2210 |  | AV2209 |  | 0 | 65535 |  |  | Zone 13 - Min. inlet air quantity, VAV damper 2 [1/100 %]
0x339E | ZoneModule 13 - VAV Supply 2 Max. Air Flow | m3/h | 4x2211 |  | AV2210 |  | 0 | 65535 |  |  | Zone 13 - Max. inlet air quantity, VAV damper 2 [1/100 %]
| ZoneModule 13 - VAV Extract Min. Air Flow | m3/h | 4x2212 |  | AV2211 |  | 0 | 65535 |  |  | Zone 13 - Min. exhaust air quantity [1/100 %]
| ZoneModule 13 - VAV Extract Max. Air Flow | m3/h | 4x2213 |  | AV2212 |  | 0 | 65535 |  |  | Zone 13 - Max. exhaust air quantity [1/100 %]
| ZoneModule 13 - VAV Supply 1 Nominal Air Flow | m3/h | 4x2214 | 3.30 | AV2213 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 1 actuator
| ZoneModule 13 - VAV Supply 2 Nominal Air Flow | m3/h | 4x2215 | 3.30 | AV2214 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 2 actuator
| ZoneModule 13 - VAV Extract Nominal Air Flow | m3/h | 4x2216 | 3.30 | AV2215 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Extract actuator
| ZoneModule 13 - Room Panel Low Air Flow | % | 4x2217 | 3.30 | AV2216 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “Low”
| ZoneModule 13 - Room Panel High Air Flow | % | 4x2218 | 3.30 | AV2217 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “High”
| ZoneModule 13 - Room Panel Override Timeout | min | 4x2219 | 3.30 | AV2218 | 3.30 | 10 | 90 |  |  | Time in minutes after which override from RPT will be reset
| ZoneModule 13 - Heat Valve Max. Flow | l/h | 4x2220 | 3.30 | AV2219 | 3.30 | 0 | 65535 |  |  | Maximum flow for Heating Valve (if actuator supports flow measurements)
| ZoneModule 13 - Cool Valve Max. Flow | l/h | 4x2221 | 3.30 | AV2220 | 3.30 | 0 | 65535 |  |  | Maximum flow for Cooling Valve (if actuator supports flow measurements)
| ZoneModule 13 - VAV Extract2 Nominal Air Flow | m3/h | 4x2223 | 3.40 | AV2222 | 3.40 | 0 | 65535 |  |  | Zone 13 - Nominal air flow of the Extract2 actuator
| ZoneModule 13 - VAV Extract2 Min. Air Flow | m3/h | 4x2224 | 3.40 | AV2223 | 3.40 | 0 | 65535 |  |  | Zone 13 - Min. Extract2 air quantity [1/100 %]
| ZoneModule 13 - VAV Extract2 Max. Air Flow | m3/h | 4x2225 | 3.40 | AV2224 | 3.40 | 0 | 65535 |  |  | Zone 13 - Max. Extract2 air quantity [1/100 %]
| ZoneModule 14 - Room Temperature Setpoint | °C | 4x2302 |  | AV2301 |  | 1000 | 4500 |  |  | Zone 14 - Setpoint for room temperature [1/100 °C]
| ZoneModule 14 - Minimum Supply Temperature | °C | 4x2303 |  | AV2302 |  | 1000 | 3000 |  |  | Zone 14 - Setpoint for min. inlet temperature [1/100 °C]
| ZoneModule 14 - Maximum Supply Temperature | °C | 4x2304 |  | AV2303 |  | 1000 | 6000 |  |  | Zone 14 - Setpoint for max. inlet temperature [1/100 °C]
| ZoneModule 14 - Room CO2 Setpoint | ppm | 4x2305 |  | AV2304 |  | 100 | 5000 |  |  | Zone 14 - Setpoint for CO2 [ppm]
| ZoneModule 14 - Room RH Setpoint | % | 4x2306 |  | AV2305 |  | 0 | 10000 |  |  | Zone 14 - Setpoint for relative humidity [1/100 %rh]
| ZoneModule 14 - VAV Supply PIR Min. Air Flow | m3/h | 4x2307 |  | AV2306 |  | 0 | 65535 |  |  | Zone 14 - Min. inlet air quantity with PIR active [1/100 %]
| ZoneModule 14 - VAV Supply 1 Min. Air Flow | m3/h | 4x2308 |  | AV2307 |  | 0 | 65535 |  |  | Zone 14 - Min. inlet air quantity, VAV damper 1 [1/100 %]
| ZoneModule 14 - VAV Supply 1 Max. Air Flow | m3/h | 4x2309 |  | AV2308 |  | 0 | 65535 |  |  | Zone 14 - Max. inlet air quantity, VAV damper 1 [1/100 %]
| ZoneModule 14 - VAV Supply 2 Min. Air Flow | m3/h | 4x2310 |  | AV2309 |  | 0 | 65535 |  |  | Zone 14 - Min. inlet air quantity, VAV damper 2 [1/100 %]
| ZoneModule 14 - VAV Supply 2 Max. Air Flow | m3/h | 4x2311 |  | AV2310 |  | 0 | 65535 |  |  | Zone 14 - Max. inlet air quantity, VAV damper 2 [1/100 %]
| ZoneModule 14 - VAV Extract Min. Air Flow | m3/h | 4x2312 |  | AV2311 |  | 0 | 65535 |  |  | Zone 14 - Min. exhaust air quantity [1/100 %]
| ZoneModule 14 - VAV Extract Max. Air Flow | m3/h | 4x2313 |  | AV2312 |  | 0 | 65535 |  |  | Zone 14 - Max. exhaust air quantity [1/100 %]
| ZoneModule 14 - VAV Supply 1 Nominal Air Flow | m3/h | 4x2314 | 3.30 | AV2313 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 1 actuator
0x3009 | ZoneModule 14 - VAV Supply 2 Nominal Air Flow | m3/h | 4x2315 | 3.30 | AV2314 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 2 actuator
0x327D | ZoneModule 14 - VAV Extract Nominal Air Flow | m3/h | 4x2316 | 3.30 | AV2315 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Extract actuator
0x327E | ZoneModule 14 - Room Panel Low Air Flow | % | 4x2317 | 3.30 | AV2316 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “Low”
| ZoneModule 14 - Room Panel High Air Flow | % | 4x2318 | 3.30 | AV2317 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “High”
| ZoneModule 14 - Room Panel Override Timeout | min | 4x2319 | 3.30 | AV2318 | 3.30 | 10 | 90 |  |  | Time in minutes after which override from RPT will be reset
| ZoneModule 14 - Heat Valve Max. Flow | l/h | 4x2320 | 3.30 | AV2319 | 3.30 | 0 | 65535 |  |  | Maximum flow for Heating Valve (if actuator supports flow measurements)
| ZoneModule 14 - Cool Valve Max. Flow | l/h | 4x2321 | 3.30 | AV2320 | 3.30 | 0 | 65535 |  |  | Maximum flow for Cooling Valve (if actuator supports flow measurements)
| ZoneModule 14 - VAV Extract2 Nominal Air Flow | m3/h | 4x2323 | 3.40 | AV2322 | 3.40 | 0 | 65535 |  |  | Zone 14 - Nominal air flow of the Extract2 actuator
| ZoneModule 14 - VAV Extract2 Min. Air Flow | m3/h | 4x2324 | 3.40 | AV2323 | 3.40 | 0 | 65535 |  |  | Zone 14 - Min. Extract2 air quantity [1/100 %]
| ZoneModule 14 - VAV Extract2 Max. Air Flow | m3/h | 4x2325 | 3.40 | AV2324 | 3.40 | 0 | 65535 |  |  | Zone 14 - Max. Extract2 air quantity [1/100 %]
| ZoneModule 15 - Room Temperature Setpoint | °C | 4x2402 |  | AV2401 |  | 1000 | 4500 |  |  | Zone 15 - Setpoint for room temperature [1/100 °C]
| ZoneModule 15 - Minimum Supply Temperature | °C | 4x2403 |  | AV2402 |  | 1000 | 3000 |  |  | Zone 15 - Setpoint for min. inlet temperature [1/100 °C]
| ZoneModule 15 - Maximum Supply Temperature | °C | 4x2404 |  | AV2403 |  | 1000 | 6000 |  |  | Zone 15 - Setpoint for max. inlet temperature [1/100 °C]
| ZoneModule 15 - Room CO2 Setpoint | ppm | 4x2405 |  | AV2404 |  | 100 | 5000 |  |  | Zone 15 - Setpoint for CO2 [ppm]
| ZoneModule 15 - Room RH Setpoint | % | 4x2406 |  | AV2405 |  | 0 | 10000 |  |  | Zone 15 - Setpoint for relative humidity [1/100 %rh]
| ZoneModule 15 - VAV Supply PIR Min. Air Flow | m3/h | 4x2407 |  | AV2406 |  | 0 | 65535 |  |  | Zone 15 - Min. inlet air quantity with PIR active [1/100 %]
| ZoneModule 15 - VAV Supply 1 Min. Air Flow | m3/h | 4x2408 |  | AV2407 |  | 0 | 65535 |  |  | Zone 15 - Min. inlet air quantity, VAV damper 1 [1/100 %]
| ZoneModule 15 - VAV Supply 1 Max. Air Flow | m3/h | 4x2409 |  | AV2408 |  | 0 | 65535 |  |  | Zone 15 - Max. inlet air quantity, VAV damper 1 [1/100 %]
| ZoneModule 15 - VAV Supply 2 Min. Air Flow | m3/h | 4x2410 |  | AV2409 |  | 0 | 65535 |  |  | Zone 15 - Min. inlet air quantity, VAV damper 2 [1/100 %]
| ZoneModule 15 - VAV Supply 2 Max. Air Flow | m3/h | 4x2411 |  | AV2410 |  | 0 | 65535 |  |  | Zone 15 - Max. inlet air quantity, VAV damper 2 [1/100 %]
| ZoneModule 15 - VAV Extract Min. Air Flow | m3/h | 4x2412 |  | AV2411 |  | 0 | 65535 |  |  | Zone 15 - Min. exhaust air quantity [1/100 %]
| ZoneModule 15 - VAV Extract Max. Air Flow | m3/h | 4x2413 |  | AV2412 |  | 0 | 65535 |  |  | Zone 15 - Max. exhaust air quantity [1/100 %]
| ZoneModule 15 - VAV Supply 1 Nominal Air Flow | m3/h | 4x2414 | 3.30 | AV2413 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 1 actuator
| ZoneModule 15 - VAV Supply 2 Nominal Air Flow | m3/h | 4x2415 | 3.30 | AV2414 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 2 actuator
| ZoneModule 15 - VAV Extract Nominal Air Flow | m3/h | 4x2416 | 3.30 | AV2415 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Extract actuator
| ZoneModule 15 - Room Panel Low Air Flow | % | 4x2417 | 3.30 | AV2416 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “Low”
| ZoneModule 15 - Room Panel High Air Flow | % | 4x2418 | 3.30 | AV2417 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “High”
| ZoneModule 15 - Room Panel Override Timeout | min | 4x2419 | 3.30 | AV2418 | 3.30 | 10 | 90 |  |  | Time in minutes after which override from RPT will be reset
| ZoneModule 15 - Heat Valve Max. Flow | l/h | 4x2420 | 3.30 | AV2419 | 3.30 | 0 | 65535 |  |  | Maximum flow for Heating Valve (if actuator supports flow measurements)
| ZoneModule 15 - Cool Valve Max. Flow | l/h | 4x2421 | 3.30 | AV2420 | 3.30 | 0 | 65535 |  |  | Maximum flow for Cooling Valve (if actuator supports flow measurements)
| ZoneModule 15 - VAV Extract2 Nominal Air Flow | m3/h | 4x2423 | 3.40 | AV2422 | 3.40 | 0 | 65535 |  |  | Zone 15 - Nominal air flow of the Extract2 actuator
| ZoneModule 15 - VAV Extract2 Min. Air Flow | m3/h | 4x2424 | 3.40 | AV2423 | 3.40 | 0 | 65535 |  |  | Zone 15 - Min. Extract2 air quantity [1/100 %]
| ZoneModule 15 - VAV Extract2 Max. Air Flow | m3/h | 4x2425 | 3.40 | AV2424 | 3.40 | 0 | 65535 |  |  | Zone 15 - Max. Extract2 air quantity [1/100 %]
| ZoneModule 16 - Room Temperature Setpoint | °C | 4x2502 |  | AV2501 |  | 1000 | 4500 |  |  | Zone 16 - Setpoint for room temperature [1/100 °C]
| ZoneModule 16 - Minimum Supply Temperature | °C | 4x2503 |  | AV2502 |  | 1000 | 3000 |  |  | Zone 16 - Setpoint for min. inlet temperature [1/100 °C]
| ZoneModule 16 - Maximum Supply Temperature | °C | 4x2504 |  | AV2503 |  | 1000 | 6000 |  |  | Zone 16 - Setpoint for max. inlet temperature [1/100 °C]
| ZoneModule 16 - Room CO2 Setpoint | ppm | 4x2505 |  | AV2504 |  | 100 | 5000 |  |  | Zone 16 - Setpoint for CO2 [ppm]
| ZoneModule 16 - Room RH Setpoint | % | 4x2506 |  | AV2505 |  | 0 | 10000 |  |  | Zone 16 - Setpoint for relative humidity [1/100 %rh]
| ZoneModule 16 - VAV Supply PIR Min. Air Flow | m3/h | 4x2507 |  | AV2506 |  | 0 | 65535 |  |  | Zone 16 - Min. inlet air quantity with PIR active [1/100 %]
| ZoneModule 16 - VAV Supply 1 Min. Air Flow | m3/h | 4x2508 |  | AV2507 |  | 0 | 65535 |  |  | Zone 16 - Min. inlet air quantity, VAV damper 1 [1/100 %]
| ZoneModule 16 - VAV Supply 1 Max. Air Flow | m3/h | 4x2509 |  | AV2508 |  | 0 | 65535 |  |  | Zone 16 - Max. inlet air quantity, VAV damper 1 [1/100 %]
| ZoneModule 16 - VAV Supply 2 Min. Air Flow | m3/h | 4x2510 |  | AV2509 |  | 0 | 65535 |  |  | Zone 16 - Min. inlet air quantity, VAV damper 2 [1/100 %]
| ZoneModule 16 - VAV Supply 2 Max. Air Flow | m3/h | 4x2511 |  | AV2510 |  | 0 | 65535 |  |  | Zone 16 - Max. inlet air quantity, VAV damper 2 [1/100 %]
| ZoneModule 16 - VAV Extract Min. Air Flow | m3/h | 4x2512 |  | AV2511 |  | 0 | 65535 |  |  | Zone 16 - Min. exhaust air quantity [1/100 %]
| ZoneModule 16 - VAV Extract Max. Air Flow | m3/h | 4x2513 |  | AV2512 |  | 0 | 65535 |  |  | Zone 16 - Max. exhaust air quantity [1/100 %]
| ZoneModule 16 - VAV Supply 1 Nominal Air Flow | m3/h | 4x2514 | 3.30 | AV2513 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 1 actuator
| ZoneModule 16 - VAV Supply 2 Nominal Air Flow | m3/h | 4x2515 | 3.30 | AV2514 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 2 actuator
| ZoneModule 16 - VAV Extract Nominal Air Flow | m3/h | 4x2516 | 3.30 | AV2515 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Extract actuator
| ZoneModule 16 - Room Panel Low Air Flow | % | 4x2517 | 3.30 | AV2516 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “Low”
| ZoneModule 16 - Room Panel High Air Flow | % | 4x2518 | 3.30 | AV2517 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “High”
| ZoneModule 16 - Room Panel Override Timeout | min | 4x2519 | 3.30 | AV2518 | 3.30 | 10 | 90 |  |  | Time in minutes after which override from RPT will be reset
| ZoneModule 16 - Heat Valve Max. Flow | l/h | 4x2520 | 3.30 | AV2519 | 3.30 | 0 | 65535 |  |  | Maximum flow for Heating Valve (if actuator supports flow measurements)
| ZoneModule 16 - Cool Valve Max. Flow | l/h | 4x2521 | 3.30 | AV2520 | 3.30 | 0 | 65535 |  |  | Maximum flow for Cooling Valve (if actuator supports flow measurements)
| ZoneModule 16 - VAV Extract2 Nominal Air Flow | m3/h | 4x2523 | 3.40 | AV2522 | 3.40 | 0 | 65535 |  |  | Zone 16 - Nominal air flow of the Extract2 actuator
| ZoneModule 16 - VAV Extract2 Min. Air Flow | m3/h | 4x2524 | 3.40 | AV2523 | 3.40 | 0 | 65535 |  |  | Zone 16 - Min. Extract2 air quantity [1/100 %]
| ZoneModule 16 - VAV Extract2 Max. Air Flow | m3/h | 4x2525 | 3.40 | AV2524 | 3.40 | 0 | 65535 |  |  | Zone 16 - Max. Extract2 air quantity [1/100 %]
| ZoneModule 17 - Room Temperature Setpoint | °C | 4x2602 |  | AV2601 |  | 1000 | 4500 |  |  | Zone 17 - Setpoint for room temperature [1/100 °C]
| ZoneModule 17 - Minimum Supply Temperature | °C | 4x2603 |  | AV2602 |  | 1000 | 3000 |  |  | Zone 17 - Setpoint for min. inlet temperature [1/100 °C]
| ZoneModule 17 - Maximum Supply Temperature | °C | 4x2604 |  | AV2603 |  | 1000 | 6000 |  |  | Zone 17 - Setpoint for max. inlet temperature [1/100 °C]
| ZoneModule 17 - Room CO2 Setpoint | ppm | 4x2605 |  | AV2604 |  | 100 | 5000 |  |  | Zone 17 - Setpoint for CO2 [ppm]
| ZoneModule 17 - Room RH Setpoint | % | 4x2606 |  | AV2605 |  | 0 | 10000 |  |  | Zone 17 - Setpoint for relative humidity [1/100 %rh]
| ZoneModule 17 - VAV Supply PIR Min. Air Flow | m3/h | 4x2607 |  | AV2606 |  | 0 | 65535 |  |  | Zone 17 - Min. inlet air quantity with PIR active [1/100 %]
| ZoneModule 17 - VAV Supply 1 Min. Air Flow | m3/h | 4x2608 |  | AV2607 |  | 0 | 65535 |  |  | Zone 17 - Min. inlet air quantity, VAV damper 1 [1/100 %]
| ZoneModule 17 - VAV Supply 1 Max. Air Flow | m3/h | 4x2609 |  | AV2608 |  | 0 | 65535 |  |  | Zone 17 - Max. inlet air quantity, VAV damper 1 [1/100 %]
| ZoneModule 17 - VAV Supply 2 Min. Air Flow | m3/h | 4x2610 |  | AV2609 |  | 0 | 65535 |  |  | Zone 17 - Min. inlet air quantity, VAV damper 2 [1/100 %]
| ZoneModule 17 - VAV Supply 2 Max. Air Flow | m3/h | 4x2611 |  | AV2610 |  | 0 | 65535 |  |  | Zone 17 - Max. inlet air quantity, VAV damper 2 [1/100 %]
| ZoneModule 17 - VAV Extract Min. Air Flow | m3/h | 4x2612 |  | AV2611 |  | 0 | 65535 |  |  | Zone 17 - Min. exhaust air quantity [1/100 %]
| ZoneModule 17 - VAV Extract Max. Air Flow | m3/h | 4x2613 |  | AV2612 |  | 0 | 65535 |  |  | Zone 17 - Max. exhaust air quantity [1/100 %]
| ZoneModule 17 - VAV Supply 1 Nominal Air Flow | m3/h | 4x2614 | 3.30 | AV2613 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 1 actuator
| ZoneModule 17 - VAV Supply 2 Nominal Air Flow | m3/h | 4x2615 | 3.30 | AV2614 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 2 actuator
| ZoneModule 17 - VAV Extract Nominal Air Flow | m3/h | 4x2616 | 3.30 | AV2615 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Extract actuator
| ZoneModule 17 - Room Panel Low Air Flow | % | 4x2617 | 3.30 | AV2616 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “Low”
| ZoneModule 17 - Room Panel High Air Flow | % | 4x2618 | 3.30 | AV2617 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “High”
| ZoneModule 17 - Room Panel Override Timeout | min | 4x2619 | 3.30 | AV2618 | 3.30 | 10 | 90 |  |  | Time in minutes after which override from RPT will be reset
| ZoneModule 17 - Heat Valve Max. Flow | l/h | 4x2620 | 3.30 | AV2619 | 3.30 | 0 | 65535 |  |  | Maximum flow for Heating Valve (if actuator supports flow measurements)
| ZoneModule 17 - Cool Valve Max. Flow | l/h | 4x2621 | 3.30 | AV2620 | 3.30 | 0 | 65535 |  |  | Maximum flow for Cooling Valve (if actuator supports flow measurements)
| ZoneModule 17 - VAV Extract2 Nominal Air Flow | m3/h | 4x2623 | 3.40 | AV2622 | 3.40 | 0 | 65535 |  |  | Zone 17 - Nominal air flow of the Extract2 actuator
| ZoneModule 17 - VAV Extract2 Min. Air Flow | m3/h | 4x2624 | 3.40 | AV2623 | 3.40 | 0 | 65535 |  |  | Zone 17 - Min. Extract2 air quantity [1/100 %]
| ZoneModule 17 - VAV Extract2 Max. Air Flow | m3/h | 4x2625 | 3.40 | AV2624 | 3.40 | 0 | 65535 |  |  | Zone 17 - Max. Extract2 air quantity [1/100 %]
| ZoneModule 18 - Room Temperature Setpoint | °C | 4x2702 |  | AV2701 |  | 1000 | 4500 |  |  | Zone 18 - Setpoint for room temperature [1/100 °C]
| ZoneModule 18 - Minimum Supply Temperature | °C | 4x2703 |  | AV2702 |  | 1000 | 3000 |  |  | Zone 18 - Setpoint for min. inlet temperature [1/100 °C]
| ZoneModule 18 - Maximum Supply Temperature | °C | 4x2704 |  | AV2703 |  | 1000 | 6000 |  |  | Zone 18 - Setpoint for max. inlet temperature [1/100 °C]
| ZoneModule 18 - Room CO2 Setpoint | ppm | 4x2705 |  | AV2704 |  | 100 | 5000 |  |  | Zone 18 - Setpoint for CO2 [ppm]
| ZoneModule 18 - Room RH Setpoint | % | 4x2706 |  | AV2705 |  | 0 | 10000 |  |  | Zone 18 - Setpoint for relative humidity [1/100 %rh]
| ZoneModule 18 - VAV Supply PIR Min. Air Flow | m3/h | 4x2707 |  | AV2706 |  | 0 | 65535 |  |  | Zone 18 - Min. inlet air quantity with PIR active [1/100 %]
| ZoneModule 18 - VAV Supply 1 Min. Air Flow | m3/h | 4x2708 |  | AV2707 |  | 0 | 65535 |  |  | Zone 18 - Min. inlet air quantity, VAV damper 1 [1/100 %]
| ZoneModule 18 - VAV Supply 1 Max. Air Flow | m3/h | 4x2709 |  | AV2708 |  | 0 | 65535 |  |  | Zone 18 - Max. inlet air quantity, VAV damper 1 [1/100 %]
| ZoneModule 18 - VAV Supply 2 Min. Air Flow | m3/h | 4x2710 |  | AV2709 |  | 0 | 65535 |  |  | Zone 18 - Min. inlet air quantity, VAV damper 2 [1/100 %]
| ZoneModule 18 - VAV Supply 2 Max. Air Flow | m3/h | 4x2711 |  | AV2710 |  | 0 | 65535 |  |  | Zone 18 - Max. inlet air quantity, VAV damper 2 [1/100 %]
| ZoneModule 18 - VAV Extract Min. Air Flow | m3/h | 4x2712 |  | AV2711 |  | 0 | 65535 |  |  | Zone 18 - Min. exhaust air quantity [1/100 %]
| ZoneModule 18 - VAV Extract Max. Air Flow | m3/h | 4x2713 |  | AV2712 |  | 0 | 65535 |  |  | Zone 18 - Max. exhaust air quantity [1/100 %]
| ZoneModule 18 - VAV Supply 1 Nominal Air Flow | m3/h | 4x2714 | 3.30 | AV2713 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 1 actuator
| ZoneModule 18 - VAV Supply 2 Nominal Air Flow | m3/h | 4x2715 | 3.30 | AV2714 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 2 actuator
| ZoneModule 18 - VAV Extract Nominal Air Flow | m3/h | 4x2716 | 3.30 | AV2715 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Extract actuator
| ZoneModule 18 - Room Panel Low Air Flow | % | 4x2717 | 3.30 | AV2716 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “Low”
| ZoneModule 18 - Room Panel High Air Flow | % | 4x2718 | 3.30 | AV2717 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “High”
| ZoneModule 18 - Room Panel Override Timeout | min | 4x2719 | 3.30 | AV2718 | 3.30 | 10 | 90 |  |  | Time in minutes after which override from RPT will be reset
| ZoneModule 18 - Heat Valve Max. Flow | l/h | 4x2720 | 3.30 | AV2719 | 3.30 | 0 | 65535 |  |  | Maximum flow for Heating Valve (if actuator supports flow measurements)
| ZoneModule 18 - Cool Valve Max. Flow | l/h | 4x2721 | 3.30 | AV2720 | 3.30 | 0 | 65535 |  |  | Maximum flow for Cooling Valve (if actuator supports flow measurements)
| ZoneModule 18 - VAV Extract2 Nominal Air Flow | m3/h | 4x2723 | 3.40 | AV2722 | 3.40 | 0 | 65535 |  |  | Zone 18 - Nominal air flow of the Extract2 actuator
| ZoneModule 18 - VAV Extract2 Min. Air Flow | m3/h | 4x2724 | 3.40 | AV2723 | 3.40 | 0 | 65535 |  |  | Zone 18 - Min. Extract2 air quantity [1/100 %]
| ZoneModule 18 - VAV Extract2 Max. Air Flow | m3/h | 4x2725 | 3.40 | AV2724 | 3.40 | 0 | 65535 |  |  | Zone 18 - Max. Extract2 air quantity [1/100 %]
| ZoneModule 19 - Room Temperature Setpoint | °C | 4x2802 |  | AV2801 |  | 1000 | 4500 |  |  | Zone 19 - Setpoint for room temperature [1/100 °C]
| ZoneModule 19 - Minimum Supply Temperature | °C | 4x2803 |  | AV2802 |  | 1000 | 3000 |  |  | Zone 19 - Setpoint for min. inlet temperature [1/100 °C]
| ZoneModule 19 - Maximum Supply Temperature | °C | 4x2804 |  | AV2803 |  | 1000 | 6000 |  |  | Zone 19 - Setpoint for max. inlet temperature [1/100 °C]
| ZoneModule 19 - Room CO2 Setpoint | ppm | 4x2805 |  | AV2804 |  | 100 | 5000 |  |  | Zone 19 - Setpoint for CO2 [ppm]
| ZoneModule 19 - Room RH Setpoint | % | 4x2806 |  | AV2805 |  | 0 | 10000 |  |  | Zone 19 - Setpoint for relative humidity [1/100 %rh]
| ZoneModule 19 - VAV Supply PIR Min. Air Flow | m3/h | 4x2807 |  | AV2806 |  | 0 | 65535 |  |  | Zone 19 - Min. inlet air quantity with PIR active [1/100 %]
| ZoneModule 19 - VAV Supply 1 Min. Air Flow | m3/h | 4x2808 |  | AV2807 |  | 0 | 65535 |  |  | Zone 19 - Min. inlet air quantity, VAV damper 1 [1/100 %]
| ZoneModule 19 - VAV Supply 1 Max. Air Flow | m3/h | 4x2809 |  | AV2808 |  | 0 | 65535 |  |  | Zone 19 - Max. inlet air quantity, VAV damper 1 [1/100 %]
| ZoneModule 19 - VAV Supply 2 Min. Air Flow | m3/h | 4x2810 |  | AV2809 |  | 0 | 65535 |  |  | Zone 19 - Min. inlet air quantity, VAV damper 2 [1/100 %]
| ZoneModule 19 - VAV Supply 2 Max. Air Flow | m3/h | 4x2811 |  | AV2810 |  | 0 | 65535 |  |  | Zone 19 - Max. inlet air quantity, VAV damper 2 [1/100 %]
| ZoneModule 19 - VAV Extract Min. Air Flow | m3/h | 4x2812 |  | AV2811 |  | 0 | 65535 |  |  | Zone 19 - Min. exhaust air quantity [1/100 %]
| ZoneModule 19 - VAV Extract Max. Air Flow | m3/h | 4x2813 |  | AV2812 |  | 0 | 65535 |  |  | Zone 19 - Max. exhaust air quantity [1/100 %]
| ZoneModule 19 - VAV Supply 1 Nominal Air Flow | m3/h | 4x2814 |  | AV2813 |  | 0 | 65535 |  |  | Nominal air flow of the Supply 1 actuator
| ZoneModule 19 - VAV Supply 2 Nominal Air Flow | m3/h | 4x2815 |  | AV2814 |  | 0 | 65535 |  |  | Nominal air flow of the Supply 2 actuator
| ZoneModule 19 - VAV Extract Nominal Air Flow | m3/h | 4x2816 |  | AV2815 |  | 0 | 65535 |  |  | Nominal air flow of the Extract actuator
| ZoneModule 19 - Room Panel Low Air Flow | % | 4x2817 |  | AV2816 |  | 1000 | 10000 |  |  | Air flow setpoint for air mode “Low”
| ZoneModule 19 - Room Panel High Air Flow | % | 4x2818 |  | AV2817 |  | 1000 | 10000 |  |  | Air flow setpoint for air mode “High”
| ZoneModule 19 - Room Panel Override Timeout | min | 4x2819 |  | AV2818 |  | 10 | 90 |  |  | Time in minutes after which override from RPT will be reset
| ZoneModule 19 - Heat Valve Max. Flow | l/h | 4x2820 |  | AV2819 |  | 0 | 65535 |  |  | Maximum flow for Heating Valve (if actuator supports flow measurements)
| ZoneModule 19 - Cool Valve Max. Flow | l/h | 4x2821 |  | AV2820 |  | 0 | 65535 |  |  | Maximum flow for Cooling Valve (if actuator supports flow measurements)
| ZoneModule 19 - VAV Extract2 Nominal Air Flow | m3/h | 4x2823 | 3.40 | AV2822 | 3.40 | 0 | 65535 |  |  | Zone 19 - Nominal air flow of the Extract2 actuator
| ZoneModule 19 - VAV Extract2 Min. Air Flow | m3/h | 4x2824 | 3.40 | AV2823 | 3.40 | 0 | 65535 |  |  | Zone 19 - Min. Extract2 air quantity [1/100 %]
| ZoneModule 19 - VAV Extract2 Max. Air Flow | m3/h | 4x2825 | 3.40 | AV2824 | 3.40 | 0 | 65535 |  |  | Zone 19 - Max. Extract2 air quantity [1/100 %]
| ZoneModule 20 - Room Temperature Setpoint | °C | 4x2902 |  | AV2901 |  | 1000 | 4500 |  |  | Zone 20 - Setpoint for room temperature [1/100 °C]
| ZoneModule 20 - Minimum Supply Temperature | °C | 4x2903 |  | AV2902 |  | 1000 | 3000 |  |  | Zone 20 - Setpoint for min. inlet temperature [1/100 °C]
| ZoneModule 20 - Maximum Supply Temperature | °C | 4x2904 |  | AV2903 |  | 1000 | 6000 |  |  | Zone 20 - Setpoint for max. inlet temperature [1/100 °C]
| ZoneModule 20 - Room CO2 Setpoint | ppm | 4x2905 |  | AV2904 |  | 100 | 5000 |  |  | Zone 20 - Setpoint for CO2 [ppm]
| ZoneModule 20 - Room RH Setpoint | % | 4x2906 |  | AV2905 |  | 0 | 10000 |  |  | Zone 20 - Setpoint for relative humidity [1/100 %rh]
| ZoneModule 20 - VAV Supply PIR Min. Air Flow | m3/h | 4x2907 |  | AV2906 |  | 0 | 65535 |  |  | Zone 20 - Min. inlet air quantity with PIR active [1/100 %]
| ZoneModule 20 - VAV Supply 1 Min. Air Flow | m3/h | 4x2908 |  | AV2907 |  | 0 | 65535 |  |  | Zone 20 - Min. inlet air quantity, VAV damper 1 [1/100 %]
| ZoneModule 20 - VAV Supply 1 Max. Air Flow | m3/h | 4x2909 |  | AV2908 |  | 0 | 65535 |  |  | Zone 20 - Max. inlet air quantity, VAV damper 1 [1/100 %]
| ZoneModule 20 - VAV Supply 2 Min. Air Flow | m3/h | 4x2910 |  | AV2909 |  | 0 | 65535 |  |  | Zone 20 - Min. inlet air quantity, VAV damper 2 [1/100 %]
| ZoneModule 20 - VAV Supply 2 Max. Air Flow | m3/h | 4x2911 |  | AV2910 |  | 0 | 65535 |  |  | Zone 20 - Max. inlet air quantity, VAV damper 2 [1/100 %]
| ZoneModule 20 - VAV Extract Min. Air Flow | m3/h | 4x2912 |  | AV2911 |  | 0 | 65535 |  |  | Zone 20 - Min. exhaust air quantity [1/100 %]
| ZoneModule 20 - VAV Extract Max. Air Flow | m3/h | 4x2913 |  | AV2912 |  | 0 | 65535 |  |  | Zone 20 - Max. exhaust air quantity [1/100 %]
| ZoneModule 20 - VAV Supply 1 Nominal Air Flow | m3/h | 4x2914 | 3.30 | AV2913 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 1 actuator
| ZoneModule 20 - VAV Supply 2 Nominal Air Flow | m3/h | 4x2915 | 3.30 | AV2914 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 2 actuator
| ZoneModule 20 - VAV Extract Nominal Air Flow | m3/h | 4x2916 | 3.30 | AV2915 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Extract actuator
| ZoneModule 20 - Room Panel Low Air Flow | % | 4x2917 | 3.30 | AV2916 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “Low”
| ZoneModule 20 - Room Panel High Air Flow | % | 4x2918 | 3.30 | AV2917 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “High”
| ZoneModule 20 - Room Panel Override Timeout | min | 4x2919 | 3.30 | AV2918 | 3.30 | 10 | 90 |  |  | Time in minutes after which override from RPT will be reset
| ZoneModule 20 - Heat Valve Max. Flow | l/h | 4x2920 | 3.30 | AV2919 | 3.30 | 0 | 65535 |  |  | Maximum flow for Heating Valve (if actuator supports flow measurements)
| ZoneModule 20 - Cool Valve Max. Flow | l/h | 4x2921 | 3.30 | AV2920 | 3.30 | 0 | 65535 |  |  | Maximum flow for Cooling Valve (if actuator supports flow measurements)
| ZoneModule 20 - VAV Extract2 Nominal Air Flow | m3/h | 4x2923 | 3.40 | AV2922 | 3.40 | 0 | 65535 |  |  | Zone 20 - Nominal air flow of the Extract2 actuator
| ZoneModule 20 - VAV Extract2 Min. Air Flow | m3/h | 4x2924 | 3.40 | AV2923 | 3.40 | 0 | 65535 |  |  | Zone 20 - Min. Extract2 air quantity [1/100 %]
| ZoneModule 20 - VAV Extract2 Max. Air Flow | m3/h | 4x2925 | 3.40 | AV2924 | 3.40 | 0 | 65535 |  |  | Zone 20 - Max. Extract2 air quantity [1/100 %]
| ZoneModule 21 - Room Temperature Setpoint | °C | 4x3002 |  | AV3001 |  | 1000 | 4500 |  |  | Zone 21 - Setpoint for room temperature [1/100 °C]
| ZoneModule 21 - Minimum Supply Temperature | °C | 4x3003 |  | AV3002 |  | 1000 | 3000 |  |  | Zone 21 - Setpoint for min. inlet temperature [1/100 °C]
| ZoneModule 21 - Maximum Supply Temperature | °C | 4x3004 |  | AV3003 |  | 1000 | 6000 |  |  | Zone 21 - Setpoint for max. inlet temperature [1/100 °C]
| ZoneModule 21 - Room CO2 Setpoint | ppm | 4x3005 |  | AV3004 |  | 100 | 5000 |  |  | Zone 21 - Setpoint for CO2 [ppm]
| ZoneModule 21 - Room RH Setpoint | % | 4x3006 |  | AV3005 |  | 0 | 10000 |  |  | Zone 21 - Setpoint for relative humidity [1/100 %rh]
| ZoneModule 21 - VAV Supply PIR Min. Air Flow | m3/h | 4x3007 |  | AV3006 |  | 0 | 65535 |  |  | Zone 21 - Min. inlet air quantity with PIR active [1/100 %]
| ZoneModule 21 - VAV Supply 1 Min. Air Flow | m3/h | 4x3008 |  | AV3007 |  | 0 | 65535 |  |  | Zone 21 - Min. inlet air quantity, VAV damper 1 [1/100 %]
| ZoneModule 21 - VAV Supply 1 Max. Air Flow | m3/h | 4x3009 |  | AV3008 |  | 0 | 65535 |  |  | Zone 21 - Max. inlet air quantity, VAV damper 1 [1/100 %]
| ZoneModule 21 - VAV Supply 2 Min. Air Flow | m3/h | 4x3010 |  | AV3009 |  | 0 | 65535 |  |  | Zone 21 - Min. inlet air quantity, VAV damper 2 [1/100 %]
| ZoneModule 21 - VAV Supply 2 Max. Air Flow | m3/h | 4x3011 |  | AV3010 |  | 0 | 65535 |  |  | Zone 21 - Max. inlet air quantity, VAV damper 2 [1/100 %]
| ZoneModule 21 - VAV Extract Min. Air Flow | m3/h | 4x3012 |  | AV3011 |  | 0 | 65535 |  |  | Zone 21 - Min. exhaust air quantity [1/100 %]
| ZoneModule 21 - VAV Extract Max. Air Flow | m3/h | 4x3013 |  | AV3012 |  | 0 | 65535 |  |  | Zone 21 - Max. exhaust air quantity [1/100 %]
| ZoneModule 21 - VAV Supply 1 Nominal Air Flow | m3/h | 4x3014 | 3.30 | AV3013 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 1 actuator
| ZoneModule 21 - VAV Supply 2 Nominal Air Flow | m3/h | 4x3015 | 3.30 | AV3014 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 2 actuator
| ZoneModule 21 - VAV Extract Nominal Air Flow | m3/h | 4x3016 | 3.30 | AV3015 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Extract actuator
| ZoneModule 21 - Room Panel Low Air Flow | % | 4x3017 | 3.30 | AV3016 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “Low”
| ZoneModule 21 - Room Panel High Air Flow | % | 4x3018 | 3.30 | AV3017 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “High”
| ZoneModule 21 - Room Panel Override Timeout | min | 4x3019 | 3.30 | AV3018 | 3.30 | 10 | 90 |  |  | Time in minutes after which override from RPT will be reset
| ZoneModule 21 - Heat Valve Max. Flow | l/h | 4x3020 | 3.30 | AV3019 | 3.30 | 0 | 65535 |  |  | Maximum flow for Heating Valve (if actuator supports flow measurements)
| ZoneModule 21 - Cool Valve Max. Flow | l/h | 4x3021 | 3.30 | AV3020 | 3.30 | 0 | 65535 |  |  | Maximum flow for Cooling Valve (if actuator supports flow measurements)
| ZoneModule 21 - VAV Extract2 Nominal Air Flow | m3/h | 4x3023 | 3.40 | AV3022 | 3.40 | 0 | 65535 |  |  | Zone 21 - Nominal air flow of the Extract2 actuator
| ZoneModule 21 - VAV Extract2 Min. Air Flow | m3/h | 4x3024 | 3.40 | AV3023 | 3.40 | 0 | 65535 |  |  | Zone 21 - Min. Extract2 air quantity [1/100 %]
| ZoneModule 21 - VAV Extract2 Max. Air Flow | m3/h | 4x3025 | 3.40 | AV3024 | 3.40 | 0 | 65535 |  |  | Zone 21 - Max. Extract2 air quantity [1/100 %]
| ZoneModule 22 - Room Temperature Setpoint | °C | 4x3102 |  | AV3101 |  | 1000 | 4500 |  |  | Zone 22 - Setpoint for room temperature [1/100 °C]
| ZoneModule 22 - Minimum Supply Temperature | °C | 4x3103 |  | AV3102 |  | 1000 | 3000 |  |  | Zone 22 - Setpoint for min. inlet temperature [1/100 °C]
| ZoneModule 22 - Maximum Supply Temperature | °C | 4x3104 |  | AV3103 |  | 1000 | 6000 |  |  | Zone 22 - Setpoint for max. inlet temperature [1/100 °C]
| ZoneModule 22 - Room CO2 Setpoint | ppm | 4x3105 |  | AV3104 |  | 100 | 5000 |  |  | Zone 22 - Setpoint for CO2 [ppm]
| ZoneModule 22 - Room RH Setpoint | % | 4x3106 |  | AV3105 |  | 0 | 10000 |  |  | Zone 22 - Setpoint for relative humidity [1/100 %rh]
| ZoneModule 22 - VAV Supply PIR Min. Air Flow | m3/h | 4x3107 |  | AV3106 |  | 0 | 65535 |  |  | Zone 22 - Min. inlet air quantity with PIR active [1/100 %]
| ZoneModule 22 - VAV Supply 1 Min. Air Flow | m3/h | 4x3108 |  | AV3107 |  | 0 | 65535 |  |  | Zone 22 - Min. inlet air quantity, VAV damper 1 [1/100 %]
| ZoneModule 22 - VAV Supply 1 Max. Air Flow | m3/h | 4x3109 |  | AV3108 |  | 0 | 65535 |  |  | Zone 22 - Max. inlet air quantity, VAV damper 1 [1/100 %]
| ZoneModule 22 - VAV Supply 2 Min. Air Flow | m3/h | 4x3110 |  | AV3109 |  | 0 | 65535 |  |  | Zone 22 - Min. inlet air quantity, VAV damper 2 [1/100 %]
| ZoneModule 22 - VAV Supply 2 Max. Air Flow | m3/h | 4x3111 |  | AV3110 |  | 0 | 65535 |  |  | Zone 22 - Max. inlet air quantity, VAV damper 2 [1/100 %]
| ZoneModule 22 - VAV Extract Min. Air Flow | m3/h | 4x3112 |  | AV3111 |  | 0 | 65535 |  |  | Zone 22 - Min. exhaust air quantity [1/100 %]
| ZoneModule 22 - VAV Extract Max. Air Flow | m3/h | 4x3113 |  | AV3112 |  | 0 | 65535 |  |  | Zone 22 - Max. exhaust air quantity [1/100 %]
| ZoneModule 22 - VAV Supply 1 Nominal Air Flow | m3/h | 4x3114 | 3.30 | AV3113 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 1 actuator
| ZoneModule 22 - VAV Supply 2 Nominal Air Flow | m3/h | 4x3115 | 3.30 | AV3114 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 2 actuator
| ZoneModule 22 - VAV Extract Nominal Air Flow | m3/h | 4x3116 | 3.30 | AV3115 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Extract actuator
| ZoneModule 22 - Room Panel Low Air Flow | % | 4x3117 | 3.30 | AV3116 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “Low”
| ZoneModule 22 - Room Panel High Air Flow | % | 4x3118 | 3.30 | AV3117 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “High”
| ZoneModule 22 - Room Panel Override Timeout | min | 4x3119 | 3.30 | AV3118 | 3.30 | 10 | 90 |  |  | Time in minutes after which override from RPT will be reset
| ZoneModule 22 - Heat Valve Max. Flow | l/h | 4x3120 | 3.30 | AV3119 | 3.30 | 0 | 65535 |  |  | Maximum flow for Heating Valve (if actuator supports flow measurements)
| ZoneModule 22 - Cool Valve Max. Flow | l/h | 4x3121 | 3.30 | AV3120 | 3.30 | 0 | 65535 |  |  | Maximum flow for Cooling Valve (if actuator supports flow measurements)
| ZoneModule 22 - VAV Extract2 Nominal Air Flow | m3/h | 4x3123 | 3.40 | AV3122 | 3.40 | 0 | 65535 |  |  | Zone 2 - Nominal air flow of the Extract2 actuator
| ZoneModule 22 - VAV Extract2 Min. Air Flow | m3/h | 4x3124 | 3.40 | AV3123 | 3.40 | 0 | 65535 |  |  | Zone 2 - Min. Extract2 air quantity [1/100 %]
| ZoneModule 22 - VAV Extract2 Max. Air Flow | m3/h | 4x3125 | 3.40 | AV3124 | 3.40 | 0 | 65535 |  |  | Zone 2 - Max. Extract2 air quantity [1/100 %]
| ZoneModule 23 - Room Temperature Setpoint | °C | 4x3202 |  | AV3201 |  | 1000 | 4500 |  |  | Zone 23 - Setpoint for room temperature [1/100 °C]
| ZoneModule 23 - Minimum Supply Temperature | °C | 4x3203 |  | AV3202 |  | 1000 | 3000 |  |  | Zone 23 - Setpoint for min. inlet temperature [1/100 °C]
| ZoneModule 23 - Maximum Supply Temperature | °C | 4x3204 |  | AV3203 |  | 1000 | 6000 |  |  | Zone 23 - Setpoint for max. inlet temperature [1/100 °C]
| ZoneModule 23 - Room CO2 Setpoint | ppm | 4x3205 |  | AV3204 |  | 100 | 5000 |  |  | Zone 23 - Setpoint for CO2 [ppm]
| ZoneModule 23 - Room RH Setpoint | % | 4x3206 |  | AV3205 |  | 0 | 10000 |  |  | Zone 23 - Setpoint for relative humidity [1/100 %rh]
| ZoneModule 23 - VAV Supply PIR Min. Air Flow | m3/h | 4x3207 |  | AV3206 |  | 0 | 65535 |  |  | Zone 23 - Min. inlet air quantity with PIR active [1/100 %]
| ZoneModule 23 - VAV Supply 1 Min. Air Flow | m3/h | 4x3208 |  | AV3207 |  | 0 | 65535 |  |  | Zone 23 - Min. inlet air quantity, VAV damper 1 [1/100 %]
| ZoneModule 23 - VAV Supply 1 Max. Air Flow | m3/h | 4x3209 |  | AV3208 |  | 0 | 65535 |  |  | Zone 23 - Max. inlet air quantity, VAV damper 1 [1/100 %]
| ZoneModule 23 - VAV Supply 2 Min. Air Flow | m3/h | 4x3210 |  | AV3209 |  | 0 | 65535 |  |  | Zone 23 - Min. inlet air quantity, VAV damper 2 [1/100 %]
| ZoneModule 23 - VAV Supply 2 Max. Air Flow | m3/h | 4x3211 |  | AV3210 |  | 0 | 65535 |  |  | Zone 23 - Max. inlet air quantity, VAV damper 2 [1/100 %]
| ZoneModule 23 - VAV Extract Min. Air Flow | m3/h | 4x3212 |  | AV3211 |  | 0 | 65535 |  |  | Zone 23 - Min. exhaust air quantity [1/100 %]
| ZoneModule 23 - VAV Extract Max. Air Flow | m3/h | 4x3213 |  | AV3212 |  | 0 | 65535 |  |  | Zone 23 - Max. exhaust air quantity [1/100 %]
| ZoneModule 23 - VAV Supply 1 Nominal Air Flow | m3/h | 4x3214 | 3.30 | AV3213 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 1 actuator
| ZoneModule 23 - VAV Supply 2 Nominal Air Flow | m3/h | 4x3215 | 3.30 | AV3214 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 2 actuator
| ZoneModule 23 - VAV Extract Nominal Air Flow | m3/h | 4x3216 | 3.30 | AV3215 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Extract actuator
| ZoneModule 23 - Room Panel Low Air Flow | % | 4x3217 | 3.30 | AV3216 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “Low”
| ZoneModule 23 - Room Panel High Air Flow | % | 4x3218 | 3.30 | AV3217 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “High”
| ZoneModule 23 - Room Panel Override Timeout | min | 4x3219 | 3.30 | AV3218 | 3.30 | 10 | 90 |  |  | Time in minutes after which override from RPT will be reset
| ZoneModule 23 - Heat Valve Max. Flow | l/h | 4x3220 | 3.30 | AV3219 | 3.30 | 0 | 65535 |  |  | Maximum flow for Heating Valve (if actuator supports flow measurements)
| ZoneModule 23 - Cool Valve Max. Flow | l/h | 4x3221 | 3.30 | AV3220 | 3.30 | 0 | 65535 |  |  | Maximum flow for Cooling Valve (if actuator supports flow measurements)
| ZoneModule 23 - VAV Extract2 Nominal Air Flow | m3/h | 4x3223 | 3.40 | AV3222 | 3.40 | 0 | 65535 |  |  | Zone 23 - Nominal air flow of the Extract2 actuator
| ZoneModule 23 - VAV Extract2 Min. Air Flow | m3/h | 4x3224 | 3.40 | AV3223 | 3.40 | 0 | 65535 |  |  | Zone 23 - Min. Extract2 air quantity [1/100 %]
| ZoneModule 23 - VAV Extract2 Max. Air Flow | m3/h | 4x3225 | 3.40 | AV3224 | 3.40 | 0 | 65535 |  |  | Zone 23 - Max. Extract2 air quantity [1/100 %]
| ZoneModule 24 - Room Temperature Setpoint | °C | 4x3302 |  | AV3301 |  | 1000 | 4500 |  |  | Zone 24 - Setpoint for room temperature [1/100 °C]
| ZoneModule 24 - Minimum Supply Temperature | °C | 4x3303 |  | AV3302 |  | 1000 | 3000 |  |  | Zone 24 - Setpoint for min. inlet temperature [1/100 °C]
| ZoneModule 24 - Maximum Supply Temperature | °C | 4x3304 |  | AV3303 |  | 1000 | 6000 |  |  | Zone 24 - Setpoint for max. inlet temperature [1/100 °C]
| ZoneModule 24 - Room CO2 Setpoint | ppm | 4x3305 |  | AV3304 |  | 100 | 5000 |  |  | Zone 24 - Setpoint for CO2 [ppm]
| ZoneModule 24 - Room RH Setpoint | % | 4x3306 |  | AV3305 |  | 0 | 10000 |  |  | Zone 24 - Setpoint for relative humidity [1/100 %rh]
| ZoneModule 24 - VAV Supply PIR Min. Air Flow | m3/h | 4x3307 |  | AV3306 |  | 0 | 65535 |  |  | Zone 24 - Min. inlet air quantity with PIR active [1/100 %]
| ZoneModule 24 - VAV Supply 1 Min. Air Flow | m3/h | 4x3308 |  | AV3307 |  | 0 | 65535 |  |  | Zone 24 - Min. inlet air quantity, VAV damper 1 [1/100 %]
| ZoneModule 24 - VAV Supply 1 Max. Air Flow | m3/h | 4x3309 |  | AV3308 |  | 0 | 65535 |  |  | Zone 24 - Max. inlet air quantity, VAV damper 1 [1/100 %]
| ZoneModule 24 - VAV Supply 2 Min. Air Flow | m3/h | 4x3310 |  | AV3309 |  | 0 | 65535 |  |  | Zone 24 - Min. inlet air quantity, VAV damper 2 [1/100 %]
| ZoneModule 24 - VAV Supply 2 Max. Air Flow | m3/h | 4x3311 |  | AV3310 |  | 0 | 65535 |  |  | Zone 24 - Max. inlet air quantity, VAV damper 2 [1/100 %]
| ZoneModule 24 - VAV Extract Min. Air Flow | m3/h | 4x3312 |  | AV3311 |  | 0 | 65535 |  |  | Zone 24 - Min. exhaust air quantity [1/100 %]
| ZoneModule 24 - VAV Extract Max. Air Flow | m3/h | 4x3313 |  | AV3312 |  | 0 | 65535 |  |  | Zone 24 - Max. exhaust air quantity [1/100 %]
| ZoneModule 24 - VAV Supply 1 Nominal Air Flow | m3/h | 4x3314 | 3.30 | AV3313 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 1 actuator
| ZoneModule 24 - VAV Supply 2 Nominal Air Flow | m3/h | 4x3315 | 3.30 | AV3314 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 2 actuator
| ZoneModule 24 - VAV Extract Nominal Air Flow | m3/h | 4x3316 | 3.30 | AV3315 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Extract actuator
| ZoneModule 24 - Room Panel Low Air Flow | % | 4x3317 | 3.30 | AV3316 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “Low”
| ZoneModule 24 - Room Panel High Air Flow | % | 4x3318 | 3.30 | AV3317 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “High”
| ZoneModule 24 - Room Panel Override Timeout | min | 4x3319 | 3.30 | AV3318 | 3.30 | 10 | 90 |  |  | Time in minutes after which override from RPT will be reset
| ZoneModule 24 - Heat Valve Max. Flow | l/h | 4x3320 | 3.30 | AV3319 | 3.30 | 0 | 65535 |  |  | Maximum flow for Heating Valve (if actuator supports flow measurements)
| ZoneModule 24 - Cool Valve Max. Flow | l/h | 4x3321 | 3.30 | AV3320 | 3.30 | 0 | 65535 |  |  | Maximum flow for Cooling Valve (if actuator supports flow measurements)
| ZoneModule 24 - VAV Extract2 Nominal Air Flow | m3/h | 4x3323 | 3.40 | AV3322 | 3.40 | 0 | 65535 |  |  | Zone 24 - Nominal air flow of the Extract2 actuator
| ZoneModule 24 - VAV Extract2 Min. Air Flow | m3/h | 4x3324 | 3.40 | AV3323 | 3.40 | 0 | 65535 |  |  | Zone 24 - Min. Extract2 air quantity [1/100 %]
| ZoneModule 24 - VAV Extract2 Max. Air Flow | m3/h | 4x3325 | 3.40 | AV3324 | 3.40 | 0 | 65535 |  |  | Zone 24 - Max. Extract2 air quantity [1/100 %]
| ZoneModule 25 - Room Temperature Setpoint | °C | 4x3402 |  | AV3401 |  | 1000 | 4500 |  |  | Zone 25 - Setpoint for room temperature [1/100 °C]
| ZoneModule 25 - Minimum Supply Temperature | °C | 4x3403 |  | AV3402 |  | 1000 | 3000 |  |  | Zone 25 - Setpoint for min. inlet temperature [1/100 °C]
| ZoneModule 25 - Maximum Supply Temperature | °C | 4x3404 |  | AV3403 |  | 1000 | 6000 |  |  | Zone 25 - Setpoint for max. inlet temperature [1/100 °C]
| ZoneModule 25 - Room CO2 Setpoint | ppm | 4x3405 |  | AV3404 |  | 100 | 5000 |  |  | Zone 25 - Setpoint for CO2 [ppm]
| ZoneModule 25 - Room RH Setpoint | % | 4x3406 |  | AV3405 |  | 0 | 10000 |  |  | Zone 25 - Setpoint for relative humidity [1/100 %rh]
| ZoneModule 25 - VAV Supply PIR Min. Air Flow | m3/h | 4x3407 |  | AV3406 |  | 0 | 65535 |  |  | Zone 25 - Min. inlet air quantity with PIR active [1/100 %]
| ZoneModule 25 - VAV Supply 1 Min. Air Flow | m3/h | 4x3408 |  | AV3407 |  | 0 | 65535 |  |  | Zone 25 - Min. inlet air quantity, VAV damper 1 [1/100 %]
| ZoneModule 25 - VAV Supply 1 Max. Air Flow | m3/h | 4x3409 |  | AV3408 |  | 0 | 65535 |  |  | Zone 25 - Max. inlet air quantity, VAV damper 1 [1/100 %]
| ZoneModule 25 - VAV Supply 2 Min. Air Flow | m3/h | 4x3410 |  | AV3409 |  | 0 | 65535 |  |  | Zone 25 - Min. inlet air quantity, VAV damper 2 [1/100 %]
| ZoneModule 25 - VAV Supply 2 Max. Air Flow | m3/h | 4x3411 |  | AV3410 |  | 0 | 65535 |  |  | Zone 25 - Max. inlet air quantity, VAV damper 2 [1/100 %]
| ZoneModule 25 - VAV Extract Min. Air Flow | m3/h | 4x3412 |  | AV3411 |  | 0 | 65535 |  |  | Zone 25 - Min. exhaust air quantity [1/100 %]
| ZoneModule 25 - VAV Extract Max. Air Flow | m3/h | 4x3413 |  | AV3412 |  | 0 | 65535 |  |  | Zone 25 - Max. exhaust air quantity [1/100 %]
| ZoneModule 25 - VAV Supply 1 Nominal Air Flow | m3/h | 4x3414 | 3.30 | AV3413 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 1 actuator
| ZoneModule 25 - VAV Supply 2 Nominal Air Flow | m3/h | 4x3415 | 3.30 | AV3414 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Supply 2 actuator
| ZoneModule 25 - VAV Extract Nominal Air Flow | m3/h | 4x3416 | 3.30 | AV3415 | 3.30 | 0 | 65535 |  |  | Nominal air flow of the Extract actuator
| ZoneModule 25 - Room Panel Low Air Flow | % | 4x3417 | 3.30 | AV3416 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “Low”
| ZoneModule 25 - Room Panel High Air Flow | % | 4x3418 | 3.30 | AV3417 | 3.30 | 1000 | 10000 |  |  | Air flow setpoint for air mode “High”
| ZoneModule 25 - Room Panel Override Timeout | min | 4x3419 | 3.30 | AV3418 | 3.30 | 10 | 90 |  |  | Time in minutes after which override from RPT will be reset
| ZoneModule 25 - Heat Valve Max. Flow | l/h | 4x3420 | 3.30 | AV3419 | 3.30 | 0 | 65535 |  |  | Maximum flow for Heating Valve (if actuator supports flow measurements)
| ZoneModule 25 - Cool Valve Max. Flow | l/h | 4x3421 | 3.30 | AV3420 | 3.30 | 0 | 65535 |  |  | Maximum flow for Cooling Valve (if actuator supports flow measurements)
| ZoneModule 25 - VAV Extract2 Nominal Air Flow | m3/h | 4x3423 | 3.40 | AV3422 | 3.40 | 0 | 65535 |  |  | Zone 25 - Nominal air flow of the Extract2 actuator
| ZoneModule 25 - VAV Extract2 Min. Air Flow | m3/h | 4x3424 | 3.40 | AV3423 | 3.40 | 0 | 65535 |  |  | Zone 25 - Min. Extract2 air quantity [1/100 %]
| ZoneModule 25 - VAV Extract2 Max. Air Flow | m3/h | 4x3425 | 3.40 | AV3424 | 3.40 | 0 | 65535 |  |  | Zone 25 - Max. Extract2 air quantity [1/100 %]
Note on D3: Jens B. Antonsen: Registers start at no. 1. Adresses start at no. 0. A typical mistake is R/W to a neighbour register.
Note on E3: Jens B. Antonsen: Number: Register is available in this software version and higher versions. x.xx: Register is available in this software and some lower versions.
Note on G3: Jens B. Antonsen: Number: Parameter is available in this software version and higher versions. x.xx: Parameter is available in this software and some lower versions.
Note on H3: Jens B. Antonsen: Minimum value. Lower values will be ignored.
Note on I3: Jens B. Antonsen: Maximum value. Higher values will be ignored.

## Bit Map Alarm overview
BitMap1 | Alarm no. | Alarm description
Bit no.1 | 301 | VAV Extract 1 Connection Error
Bit no.2 | 302 | VAV Supply 1 Connection Error
Bit no.3 | 303 | VAV Supply 2 Connection Error
Bit no.4 | 304 | Cooling Actuator Connection Error
Bit no.5 | 305 | Heating Actuator Connection Error
Bit no.6 | 306 | Combined Heating/Cooling Actuator Connection Error
Bit no.7 | 307 | Window Contact/Frost Protection Sensor Connection Error
Bit no.8 | 308 | PIR Sensor Connection Error
Bit no.9 | 309 | Room Temperature Sensor Removed
Bit no.10 | 310 | Supply Temperature Sensor Removed
Bit no.11 | 311 | Setpoint Offset Sensor Connection Error
Bit no.12 | 312 | CO2/VOC Sensor Connection Error
Bit no.13 | 313 | RH% Sensor Connection Error
Bit no.14 | 314 | Room Temperature Sensor Shorted
Bit no.15 | 315 | Supply Temperature Sensor Shorted
Bit no.16 | 316 | VAV Extract 1 Mechanical Error
BitMap2 | Alarm no. | 1. Info
Bit no.1 | 317 | VAV Supply 1 Mechanical Error
Bit no.2 | 318 | VAV Supply 2 Mechanical Error
Bit no.3 | 319 | Cooling Actuator Mechanical Error
Bit no.4 | 320 | Heating Actuator Mechanical Error
Bit no.5 | 321 | Combined Heating/Cooling Actuator Mechanical Error
Bit no.6 | 323 | Unsupported Actuator Type Detected
Bit no.7 | 324 | Unsupported Room Panel Software Version
Bit no.8 | 326 | Room Temperature Sensor Removed
Bit no.9 | 327 | Ext. Heater 1 Alarm Input Active
Bit no.10 | 328 | Ext. Heater 2 Alarm Input Active
Bit no.11 | 329 | Ext. Heater 1 Temperature Sensor Error
Bit no.12 | 330 | Ext. Heater 2 Temperature Sensor Error
Bit no.13 | 331 | Ext. Module Connection Error
Bit no.14 | 332 | VAV Extract 2 Connection Error
Bit no.15 | 333 | VAV Extract 2 Mechanical Error
Bit no.16 | 334 | MP-Bus Overload
BitMap3 | Alarm no. | 1. Info
Bit no.1 | 335 | MPL-09 Connection Error
Bit no.2 | 336 | MPL-10 Connection Error
Bit no.3 | 337 | MPL-11 Connection Error
Bit no.4 | 338 | MPL-12 Connection Error
Bit no.5 | 339 | MPL-13 Connection Error
Bit no.6 | 340 | MPL-14 Connection Error
Bit no.7 | 341 | MPL-15 Connection Error
Bit no.8 | 342 | MPL-16 Connection Error
Bit no.9 | 343 | For future use
Bit no.10 | 344 | For future use
Bit no.11 | 345 | For future use
Bit no.12 | 346 | For future use
Bit no.13 | 347 | For future use
Bit no.14 | 348 | For future use
Bit no.15 | 349 | For future use
Bit no.16 | 350 | For future use
BitMap4 | Alarm no. | 1. Info
Bit no.1 | 351 | For future use
Bit no.2 | 352 | For future use
Bit no.3 | 353 | For future use
Bit no.4 | 354 | For future use
Bit no.5 | 355 | For future use
Bit no.6 | 356 | For future use
Bit no.7 | 357 | For future use
Bit no.8 | 358 | For future use
Bit no.9 | 359 | For future use
Bit no.10 | 360 | For future use
Bit no.11 | 361 | For future use
Bit no.12 | 362 | For future use
Bit no.13 | 363 | For future use
Bit no.14 | 364 | For future use
Bit no.15 | 365 | For future use
Bit no.16 | 366 | For future use